ARM-EVAC® 105

Central Filter Unit

# MANUAL NO. 8881-0990

# REV. A

(230v Systems only)

## TABLE OF CONTENTS

Safety  …………………………………………………………………….		3

Introduction ………………………………………………………………		4

Specification. …………………………………………………………….		4

Features ………………………………………………………………….		5

Set-Up…………………………………………………………………….		5

Operation…………………………………………………………………                        6

Maintenance ……………………………………………………………..		6

Troubleshooting…………………………………………………………..		6

Filter Replacement & Part Numbers………………………………………		7-8

Warranty……………………………………………………………………	             9

Equipment Registration Form …………………………………………..		10

##### WARNING

Read the safety & set-up information sections in this manual thoroughly before installing and using your fume extraction system.

## Safety

PACE Fume Extraction systems are designed to reduce the level of harmful contaminants from the work environment and to assist in the achievement of recommended health and safety requirements for local exhaust ventilation and contaminant removal.  Be sure to follow all safety guidelines contained herein and precautions contained in other relevant product safety literature (i.e., Material Safety Data Sheets) provided with the substances and equipment producing the fumes to be extracted.

Disclaimer

PACE hereby disclaims all responsibility for any personal injury, property damage, fine, citation or penalty imposed by any government or private entity which results from any use, misuse or mis-application of this product, failure of the user to regularly maintain the product according to the recommended guidelines, or failure to adequately monitor fume extraction exhaust air and the ambient workplace air for the presence of harmful levels of gases, fumes and particulates.

Compliance with all applicable environmental and personal safety regulations is the sole responsibility of the user and adequate self-monitoring of exhaust air released into the atmosphere or the workplace as well as monitoring of the ambient workplace air is strongly recommended.  To insure continued effective performance, the following guidelines must be followed.

Dangers

- PACE Fume Extractors are not intended to be used as a substitute for devices such as personal protective respirators which are designed to remove poorly adsorbed substances including carbon monoxide, methane, hydrogen, acetylene and other gases.  Risk of serious injury or death, fire or explosion may result from improper use.  If in doubt, contact your industrial hygienist or PACE.

- Never use PACE Fume Extraction Systems to extract fumes from highly flammable liquids and gases such as Ether, Gasoline (Petrol) and others.  Risk of serious injury, death, fire or explosion may result.

- High concentrations or airborne contaminants such as Methyl Ethyl Ketone, Cyclohexone, Ozone and others when contacted with activated carbon, can undergo oxidation, decomposition or polymerization resulting in exothermic reactions or heat generation.  PACE Fume Extraction Systems must not be used to extract fumes from these substances when high concentrations are present.

- Failure to comply with the application and maintenance guidelines, filter replacement schedules, monitoring recommendations and safety guidelines contained herein and in other relevant product safety literature (i.e., Material Safety Data Sheets) provided with the substances and equipment producing the fumes to be extracted could result in risk of serious injury, fire or explosion.

## Introduction

Solder Fume removal when hand soldering is an often-overlooked work place hazard.  Medical research has confirmed that there is an increase incidence of occupational asthma, chronic bronchitis, allergic reactions and other health related effects associated with exposure to solder/flux fumes in the electronics industry.

The PACE Arm-Evac 105 Central Filter Unit represents the latest technology in affordable fume extraction.  It features a brushless motor along with a filtration process which includes a pre-filter for course particle removal, and a HEPA-Type Particulate/Gas Filter cartridge for efficient filtration.  Optional filters are also available:

1) A General Purpose Filter for normal Soldering applications, 2) A Clean room Filter for use in clean room environments and 3) An Adhesive Filter for removing fumes produced from light gluing applications and 4) An Economy Foam filter for larger applications such as sanding, Benchtop machining & grinding.

The Arm-Evac 105 Central Filter Unit uses specially designed extraction accessories that can be conveniently mounted on any workbench or tabletop.  The Arm-Evac 105 is designed to extract fumes from one or two work stations.

Specifications

Arm-Evac 105System Part Numbers				8888-0105 220/240V 50hz

8888-0110 110V, 60hz

Flow Rate with standard filter*	Single inlet: 220m³/h (130cfm)

Dual Inlet: 118m³/h (70cfm) per inlet

Flow Rate with Optional Cleanroom Filter*	Single inlet: 187m³/h (110cfm)

Dual inlet: 105m³/h (62cfm) per inlet

Noise Level*							55dbA at 2 metres

Weight								11.5Kg (25.3lbs)

Size H x W x D							365 x 290 x 290mm

(14.25” x 11.5” x 11.5”)

Housing	20 guage Steel (static safe)

Number of inlets	Two 75mm (3”)

# of Collection accessories	Two 65mm (2.5”) or 75mm (3”)

Maximum duct run	2.5m (8’) per inlet

Standard Filter							General Purpose HEPA Filter

Filtration options						Cleanroom Filter

## Adhesive Filter

Extended Life Filter

Economy Filter

###### Environmental Specifications

## Ambient operating temperature					0ºC to 50º (32ºF to 122ºF)

Storage temperature						-40ºC to 125ºC (-40ºF to 257ºF)

Ambient operating humidity	90% relative humidity max non-condensing

Storage humidity	90% relative humidity max non-condensing

*Airflow and noise levels are nominal figures and will vary based on voltage

## Features

Arm-Evac 105 Central Filter Unit

1.	On/Off Switch

2.	75mm (3”) inlets/Lid

3.	Lid clasps

2

1

3

Fig.1	Arm-Evac 105 Central Filter Unit

###### Set up

1.	The Arm-Evac 105 has been designed for ease of use and maximum installation flexibility in mind.  The major considerations for placement of the unit are:

Exhaust Port:	This is located on the right side of the unit.  When positioning the unit, make sure that the exhaust port is not blocked or that airflow from the exhaust port is not restricted in any way.

Proximity to work area:	The unit should be placed as close to the work area as possible.  Do not create any sharp bends in the flexible hose (optional), as this will reduce airflow.

Unit Location	The filtration unit should be located so that it will not block aisleways or impede normal operating traffic of material handling pathways.  It is important to position the unit in such a way that allos for proper clearance to remove the lid and replace the filter as needed.

2.	The Arm-Evac 105 will plug into a standard 110v or 230v electrical outlet.  A line cord is provided with each system.

###### Operation

1.	Remove Arm-Evac 105 from packaging and place in suitable position.

2.	Plug power cord (supplied) into receptacle at left side of unit, ensuring that it is connected to a properly grounded outlet.

3.	Fit appropriate fume collection accessory.

4.	Turn on the Arm-Evac 105.

###### Maintenance

Fuses:	The fuse is located in a sliding tray at the left side of the unit, just below the power receptacle.  Each Arm-Evac is supplied with one replacement fuse, also located in the sliding tray.

Replacement fuses are available for the Arm-Evac 105 systems in packages of 5 fuses.  3.15A fuse for 8888-0105 are available as 8884-9966-P5 and 8A fuse for 8888-0110 are available as 8884-9961-P5.

Fan Assy:	The Arm-Evac 105 is fitted with a brush-less, single inlet  fan assembly, which does not require routine maintenance.  However, for long lasting trouble free operation, the motor should be oiled every six months with SAE 20  It is important that fume extractor filters are changed on a regular basis to protect the fan assembly.

A vent is located on the right side of the unit to allow the cleaned air to return to the workplace.  Do not cover this vent as this may cause damage to the fan assembly.

Never operate the Arm-Evac 105 without filters installed.

Troubleshooting

| Symptom | Possible Cause | Solution |
| --- | --- | --- |
| System does not power up | No power supplied to unit | Check power cord |
|  |  | Is connected and power |
|  |  | Is switched on. |
| Reduced Airflow | Filter blocked, Optional | Check & change filter(s) |
|  | Arm attachment not installed | if req, check Arm |
|  | correctly | attachment connection. |

If the unit does not work after checking the above, please contact PACE, or your Authorized PACE Distributor if outside U.S.

Filter Replacement & Spare Parts

PACE Fume Extraction Systems are equipped with filters designed to capture particulates and noxious gases and odors that are present in the air being filtered.  Over time, the filters will become clogged, impeding airflow through the system and the capacity of the gas filter (if fitted) will be reached, reducing its ability to continue to neutralize and adsorb noxious gases and odors.

Do not attempt to clean any PACE fume extraction filters for reuse.  Cleaning the filters will severely damage the filter media and, consequently, the filter’s performance.  This will result in unfiltered, contaminated air being returned to the working environment.  Unfiltered air can also damage the fan assembly.

To ensure the highest level of performance, use only PACE replacement filters in your PACE Fume Extraction System.

Arm-Evac 105 Pre-Filter

The pre-filter removes coarse particles from the air.  In general, the pre-filter must be changed on a monthly basis.  However, depending on your particular process, the filter may need to be changed more or less frequently.  A visual inspection on a weekly basis is recommended.

Replacing the Pre-Filter

1.	Remove the Filter access cover (lid)

2.          Remove the old Pre-Filter

3.	Install a new Pre-Filter.  Be sure that the blue side of the filter faces up.

4.	Attach lid.

5.	Dispose of he used Pre-Filter properly

Arm-Evac 105 standard filter

The standard filter cartridge removes particulates from the air and captures noxious odours & gases.  In general, the filter cartridge must be changed every 6 to 9 months based on a typical 8 hour work day.  However, depending on your particular process, the filter cartridge may need to be changed more or less frequently.

Replacing the Filter cartridge

1.	Remove the lid.

2.	Remove the old filter.

3.	Install new filter.

4.	Install a new Pre-Filter.  Be sure that the blue side of the pre-filter faces up.

5.	Attach lid

6.	Dispose of old filter properly.

BE SURE the new filter cartridge is installed with the airflow arrow pointing downward.

When disposing of used filters, extreme care must be taken to comply with all applicable environmental regulations.  Carefully consult the MSDS supplied with the material(s) producing the fume.  If in doubt, check with your local Environmental Authority.

###### Replacement Filter part numbers

| Item # | Name | Description | Typical Applications | Part Number |
| --- | --- | --- | --- | --- |
| 1 | Arm-Evac 105 Pre-filter | Designed for coarse particle capture. | Used with all Arm-Evac 105 systems. | 8883-0111P5 (Pkg. Of 5) |
| 2 | Arm-Evac 105 General Purpose Filter | Comprised of HEPA filter media & gas blend media | Soldering, Pharmaceuticals, Laser Cutting/Laser Marking, Jewellery manufacture & repair. | 8883-0931 |
| 3* | Arm-Evac 105 Extended Life Pre-Filter | Designed for coarse particle capture. | Heavy-Duty Soldering operations | 8883-0938-P10(Pkg. Of 10) |
| 4* | Arm-Evac 105 Extended Life Combo HEPA/Gas Filter | Comprised of HEPA filter media & gas blend media | Heavy-Duty Soldering operations | 8883-0936 |
| 5 | Adhesives Filter | Blend of Adsorptive & Chemisorptive media. | Benchtop Adhesives Procedures, Gluing Applications, Circuit Board Cleaning, Laboratory Applications | 8883-0951 |
| 6 | Cleanroom Filter | Comprised of HEPA filter media & bonded activated carbon. | Fine particulate and gas removal in designated Cleanroom environments. | 8883-0921 |
| 7 | Economy Foam Filter | Carbon-Impregnated reticulated foam media. Designed for coarse particle capture. | Sanding applications, Benchtop Machining Operations, Benchtop Prototyping Operations, Grinding Applications. | 8883-0871 |

*These items must be used together.  NEVER use them separately!

PACE WORLDWIDE LIMITED WARRANTY

PACE warrants to the first user that Products manufactured by it and supplied hereunder are free of defects in materials and workmanship for a period of: (1) year from the date of receipt by such user. This Warranty as applied to blowers and motor pumps is limited to a period of six (6) months.  Monitors, computers and other brand equipment supplied but not manufactured by PACE are covered under their respective manufacturer’s warranty in lieu of this Warranty.

This warranty does not cover wear and tear under normal use, repair or replacement required as a result of misuse, improper application, mishandling or improper storage.  Consumable items such as tips, heaters, filters etc. which wear out under normal use are excluded.  Failure to perform recommended routine maintenance, alterations or repairs made other than in accordance with PACE’s directions, or removal or alteration of identification markings in any way will void this warranty. This warranty is available only to the first user, but the exclusions and limitations herein apply to all persons and entities.

PACE MAKES NO OTHER WARRANTY, EXPRESS OR IMPLIED, AND MAKES NO WARRANTY OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.

PACE will, at its option, repair or replace any defective products at its facility or other location approved by it at no charge to user, or provide parts without charge for installation by the user in the field at user’s expense and risk.  User will be responsible for all costs of shipping equipment to PACE or other location for warranty service.

EXCEPT FOR THE REMEDY ABOVE DESCRIBED, UNLESS OTHERIWSE REQUIRED BY APPLICABLE LAW, PACE WILL HAVE NO OTHER OBLIGATION WITH REGARD TO ANY BREACH OF WARRANTY OR OTHER CLAIM WITH RESPECT TO THE PRODUCTS, OR LIABILITY FOR ANY DIRECT, INDIRECT, CONSEQUENTIAL, OR INCIDENTAL LOSS OR DAMAGE CAUSED BY OR OCCURRING IN CONNECTION WITH ANY OF THE PRODUCTS.

Warranty service may be obtained by contacting the appropriate PACE Company or local Authorised PACE distributor as set forth below to determine if return of any item is required, of if repairs can be made by the user in the field.

Defective products may not be returned to PACE without a Service Authorization (“SA”) Number.

Any warranty or other claim with respect to the products must be made in writing delivered to PACE (or local Authorised PACE Distributor for Buyers outside the USA and the United Kingdom) within a reasonable time of the expiration date of this warranty with sufficient evidence of purchase and date of receipt, otherwise user’s rights under this warranty shall be deemed waived.

For Customer’s in the USA & Canada:		For Customer’s in Europe:

PACE USA					PACE Europe Limited

9030 Junction Drive				13 Tanners Drive

Annapolis Junction				Blakelands

MD 20701					Milton Keynes

USA						MK14 5BU

United Kingdom

Tel: (301) 490-9860				(44) 01908 277666

Fax: (301) 498-3252				(44) 01908 277777

All other Customers: Local Authorized PACE Distributor

Defective products may not be returned to PACE without a Service Authorisation (“SA”) Number.  Any warranty claim with respect to the products must be made in writing delivered to PACE (of local Authorised PACE Distributor for Buyers outside the USA and the United Kingdom) within a reasonable time of the expiration date of this warranty with sufficient evidence of purchase and date of receipt, otherwise user’s rights under this warranty shall be deemed waived.

To register your purchase with PACE, fill in the form below and mail or FAX to the applicable PACE address listed above.

EQUIPMENT WARRANTY REGISTRATION CARD

Date

Model No.			 	Serial No.			Of Receipt

Purchased from

Company Name

Mailing Address

Telephone number with area code

Fax Number with area code

Internet Address

Full Name

Authorized Signature, Title

www.paceworldwide.com