# SECTION 16610

## STATIC UNINTERRUPTIBLE POWER SUPPLY

GUIDE SPECIFICATIONS:

FOR 3 TO 18KVA, SINGLE PHASE, N+X POWER AND LOGIC REDUNDANT, MODULAR, UNINTERRUPTIBLE POWER SYSTEM

PART 1 - GENERAL

1.01	SUMMARY

- This specification defines the electrical and mechanical characteristics and requirements for a continuous-duty single-phase, solid-state, uninterruptible power supply system.  The uninterruptible power supply system, hereafter referred to as the UPS, shall provide high-quality AC power for sensitive electronic equipment loads with N+X power and logic capabilities with hot swappable power and battery modules to maintain maximum uptime.  The UPS shall operate in conjunction with the existing building electrical system to protect electronic equipment from power disturbances that may occur with utility power, such as voltage fluctuations, brownouts, power surges and sags.

  - SYSTEM DESCRIPTION

Standard UPS System will include a minimum of (1) Enclosure, (1) Power Module and (2) Battery Modules.  For each Power Module in the system a minimum or (2) Battery Modules (or 1 string of batteries) is required.

- Components:

  - Converter (Rectifier/Booster)

  - Inverter

  - Sealed Lead Acid Battery Modules

  - Battery Charger

  - Automatic Bypass

  - User Interface Panel

  - Serial (RS-232) Communication Interface

  - Communication Card Slots (2)

  - Remote Emergency Power Off Contacts

  - On Generator Contacts

  - On Bypass Contacts

  - Input Line Cord or Hardwired

  - Receptacles or Hardwired Output

  - (Option) Isolation

  - (Option) 20 Amp Charger Module

  - (Option) Rackmounting Kit for 3 and 6 slot Enclosures

  - (Option) Caster Kit for 3 and 6 slot Enclosures

  - (Option) External Matching Battery Cabinets

  - (Option) Wall Mounted Maintenance Bypass Cabinets

  - (Option) SNMP/Web Adaptor

  - (Option) Relay Card

  - (Option) Expansion chassis including Mod buss card

- Modes of Operation:  The UPS shall operate as an on-line, double-conversion UPS with the following operations modes:

1.	Normal Mode:  During the Normal or Double Conversion Mode the rectifier shall derive power as needed from the commercial AC utility or generator source and supply filtered and regulated DC power to the on-line inverter.  The inverter shall convert the DC power to highly regulated and filtered AC power for the critical loads.

2.         Hi Efficiency Mode:  The UPS can be (manually) switched to High Efficiency Mode to optimize its efficiency (to approximately 97%) during favorable utility conditions. If the utility conditions become unfavorable the UPS will automatically switch back to Normal (double conversion) Mode to supply properly regulated and filtered AC power for the critical loads.  The UPS will automatically switch back to High Efficiency Mode when favorable utility conditions return.

3. 	Battery Mode: Upon complete utility power failure or while the UPS is manually switched to Battery Mode, the UPS shall provide power to the critical loads through the inverter, from the UPS’ internal or extended batteries.  When utility returns, the UPS shall immediately return to Normal Mode operation.

4.	Bypass Mode:  This mode can be entered into manually (to service the UPS) or automatically entered into to transfer the critical loads to commercial AC source, and bypassing the UPS’s inverter/rectifier.  This mode is automatically entered into in case of an overload or an internal UPS failure.

5.	Standby Mode:  When initially attached to a utility or other power source, the UPS shall start in this Standby Mode until the user initiates power (completes initial setup and gives the UPS ON command) to the critical load.  In this mode the UPS shall recharge the batteries, but power shall not be supplied to the critical loads.

6.	Sleep Mode:  This mode is entered into automatically is utility power is not present and the battery capacity is determined to be insufficient.  This mode is normally entered while the unit is shipping or after a low battery shutdown.  Its purpose is to protect the batteries in the UPS for longer life.

1.03	APPLICABLE STANDARDS

The UPS shall be designed in accordance with the applicable sections of the current revision of the following documents.  Where a conflict arises between these documents and statements made herein, the statements in this specification shall govern.

- UL1778, UL497A

- CSA22.2 No 107.1 and 107.2

- FCC Part 15, Subpart J, Class a

- IEEE 587/ANSI C62.41

- EN50091-2 (Emissions Class A and Harmonics)

- Australia (C-Tick)

- Japan (VCCI) Class A

- Taiwan (BCIQ) Class A

- CSA-C22.2 No 107.1

- EN50091-1-1

- EN61000-4-2,-3,-4,-5

1.04	SUBMITTALS

- Submit one copy of a concise operation and maintenance manuals (i.e. User Manual).

  - QUALIFICATIONS

- The manufacturer of the UPS shall have a minimum of ten years experience in the design, manufacture and testing of Uninterruptible Power Supplies.

- The manufacturer shall be ISO9001 registered.

### Part 2 - PRODUCTS

  - GENERAL

- Manufacturer

  - Powerware Corporation

- Model

The UPS system is a modular system consisting of an Enclosure, Power Module(s), and Battery Modules.  The system can be configured with numerous options, including:

  - Line Cords or Hard wired input

  - Numerous NEMA Receptacles or Hardwired output

  - Rackmounting kits

  - Caster Kits

  - Floor Anchoring Kits

  - Wall Mounted Maintenance Bypass Cabinets

  - External Matching Battery Cabinets

  - Galvanic Isolation

  - Several Connectivity Options

  - UNINTERRUPTIBLE POWER SUPPLY

- Converter (rectifier/booster):  Incoming power shall be filtered and converted to DC by a full-wave rectifier.  The DC power is then processed by a high-frequency converter to supply power to the inverter.   The Converter corrects the input power factor to 0.98 and draws sinusoidal current (with less than 10% THD) from the utility.  In the event of utility failure, the converter shall be supplied power without interruption from the internal of external batteries.  During normal operation, the batteries will be charged through the rectifier.

  - Overload Capacity:  The converter shall be capable of supplying up to 150% of rated load for at least 10 seconds before transferring to bypass.

- Inverter: The inverter converts the DC Power to regulated AC Power for critical loads.

  - Output Voltage: The inverter output voltage is specified in section 2.03.

  - Voltage Regulation: The inverter steady state voltage regulation is +/- 3% in steady state.

  - Frequency Control: The inverter steady state frequency regulation is +/-0.1Hz in steady state.

- Batteries: The batteries shall be sealed, lead acid, maintenance-free, high-rate discharge cells.  They will be kept fully charged by the battery charger(s) in each 3kVA Power Module and optional 20 amp charger modules.  They have an expected life of 200 complete full load discharge cycles when operated and maintained within specifications.

- Battery Charger: The battery charger(s) is responsible for charging the battery and maintaining full battery charge when AC is applied to the UPS.

- Automatic Bypass (Static bypass): The UPS shall provide an alternate path to the commercial AC or generator source in case of an overload, load fault or internal UPS failure.  This input must match the output in voltage, frequency, and grounding in order to properly utilize this feature.

- User Interface Panel:  The UPS shall provide a user-friendly interface panel, which allows the user to:  change operating modes, set system parameters, check alarm and inverter logs, etc.  This LCD display should have four languages consisting of English, Spanish, German and French.

- Serial (RS-232) Communication Interface: A 9-pin sub-D connector shall provide capability for communicating with manufacture-supplied software package.  The UPS shall also provide signals for indication of AC-Fail; On-Battery and Low-Battery statuses.

- (2) Communication card slots:  The UPS shall provide (2) Communication card slots in the back of the UPS allowing for additional connectivity options, including SNMP/Web capabilities, etc.

- Remote Emergency Power Off (EPO) connection:  The UPS shall provide a built-in landing for field connection of a Remote Emergency Power Off circuit.  Upon initiation of the REPO circuit, the UPS shall open its output relays, and disengage the battery converter, preventing power from being delivered to the attached loads.

- On Generator connection: The UPS shall provide a built-in landing for field connection to a generator.  This connection will aid the UPS in working properly with the generator.

- On Bypass connection:  The UPS shall provide a built-in landing for field connection to a maintenance bypass switch.  This connection will insure the UPS is in bypass mode prior to switching to the maintenance bypass switch.

- Input Line Cord or Hardwired to utility:  The UPS can be ordered with an input line cords or for hardwired directly to a utility.

- Receptacles or Hardwired output:  The UPS can be ordered with several different types and quantities of receptacles or ordered for Hardwired output.

- (Option) Isolation: The UPS can be ordered specially with Galvanic Isolation (split phase systems only).

- (Option) 20 Amp Charger Module(s):  The UPS can be ordered with additional 20 amp charger module(s) for extended runtime requirements or for fast recharge requirements.

- (Option) Rackmounting kit: The 3 and 6 slot UPS’s can be ordered with a rackmounting to allow mounting the UPS in a standard 19 inch rack.

- (Option) Caster kit:  The 3 and 6 slot UPS’s can be order with caster kits.

- (Option) External Matching Battery Cabinets: 6, 9 and 12 slot matching battery cabinets can be ordered for extended runtime requirements.

- (Option) Wall Mounted Maintenance Bypass Cabinets: Wall Mounted Make Before Break or Break Before Make Bypass Cabinets can be ordered as needed for use with the UPS.

- (Option) SNMP/Web Adaptor: Internal communication card providing network communication via SNMP protocol.

- (Option) Relay Card: Internal card providing dry contacts for operation with AS400 systems, etc.

2.03	SYSTEM RATINGS AND OPERATING CHARACTERISTICS

- System Input

  - Input Voltage Operation Range

    - Nominal Input Voltage range is 208-240VAC

    - Maximum Input Voltage range is 176-276VAC

  - Input Frequency

    - 45 to 65Hz

    - auto sensing

    - user selectable frequency range in 0.1Hz increments

  - Input Power Factor is 0.98

  - Input Current Distortion: 10% THD maximum at full load.

  - Inrush Current: 150% of full load input current maximum for 3 cycles

  - Surge Protection: Sustains input surges without damage per criteria listed in ANSI C62.41-1980 (IEEE 587), Category A and B

- System Output, Normal Mode

  - Nominal Output Voltage

    - Input voltages of 208/120, 240/120, 220/127, 220/110 and 200/100 VAC, single-phase, 3-wire-plus-ground (for use with Split Phase Power Modules), yield field programmable output voltages of 208/120, 240/120, 220/127, 220/110 and 200/100 VAC.

    - Input voltages of 208, 220, 230 and 240VAC single phase, 2-wire-plus-ground (for use with Universal Power Modules), yield field programmable output voltages of 208, 220, 230 and 240 volts.

  - Voltage regulation: +/-3% of selected output voltage in steady state

  - Transient Voltage Response:

    - Voltage Transient Response: +/- 3% maximum while in Double Conversion mode with resistive step loads from 0% to 50%, 50% to 100%, 100% to 50% and 50% to 0%.  Or, +/-5% maximum while in Double Conversion mode with resistive step loads from 0% to 100% or 100% to 0%.

  - Transient Recovery Time: To within 1% of steady state output voltage within 50      milliseconds

  - Voltage THD:

    - 3% Total Harmonic Distortion (THD) maximum into a 100 percent linear load

    - 5% THD maximum into a 100% non-linear load

  - Nominal Frequency: 50 or 60 Hz Auto selectable

  - Frequency Regulation:

    - Sync with line within +/-3 Hz of nominal line frequency, or

    - Transfer to battery power with frequency at +/-0.1Hz of the selected nominal frequency if out of +/-3 Hz specification.

  - Output Current:  Maximum output current (at nominal output voltage) for the UPS shall be:

    - 3kVA system:  25A @ 120V

    - 6kVA system:  50A @ 120V

    - 9kVA system:  75A @ 120V

    - 12kVA system: 100A @ 120V

    - 15kVA system: 125A @ 120V

    - 18kVA system: 150A @ 120V

  - Current Overload Capability:

    - 150% for 10 seconds

    - 300% for 12 cycles

  - Bypass:

    - Automatic bypass shall provide an alternate path to utility power in the case of overload, UPS failure and excessive transfers while in High Eff. Mode.

    - External Maintenance Bypass can be utilized with the UPS to all servicing of the UPS.  There are MBB and BBM bypass switches available.

    - Transfer time to and from any internal bypass shall be no-break.

  - Efficiency:

    - Minimum of 97% while in High Efficiency Mode

    - Nominal 88% in Normal Mode with full resistive load and fully charged batteries

- System Output, Battery Mode:

  - Nominal Output Voltage:  This shall be the user selected output voltage.  This must be entered into the UPS prior to turning the UPS on.

  - Voltage Regulation: +/-3% of selected nominal voltage

  - Transient Voltage Response

    - Voltage Transient Response: +/- 3% maximum while in Battery mode with resistive step loads from 0% to 50%, 50% to 100%, 100% to 50% and 50% to 0%.  Or, +/-5% maximum while in Battery mode with resistive step loads from 0% to 100% or 100% to 0%.

  - Transient Voltage Recovery: To within 1% of steady state output voltage within 50      milliseconds

  - Voltage THD:

    - 3% Total Harmonic Distortion (THD) maximum into a 100 percent linear load

    - 5% THD maximum into a 100% non-linear load

  - Frequency Regulation: +/-1Hz of selected nominal frequency

  - Overload Capacity:

    - 150% for 10 seconds

    - 300% for 12 cycles

- Mechanical Construction:

  - All materials and components making up the UPS shall be new, of current manufacture, and shall not have been in prior service except as required during factory testing.  The UPS shall be constructed of replaceable subassemblies.  All active electronic devices shall be solid-state.

  - The UPS unit comprised of: input converter, battery charger, inverter, bypass, and battery consisting of the appropriate number of sealed battery modules, shall be housed in a single freestanding enclosure. The UPS cabinet shall be cleaned, primed, and painted with the manufacturer's standard color.  Casters and leveling feet shall be provided as needed.

  - The UPS 3 and 6 slot Enclosures shall have provisions (kits) to easily modify the UPS to be installed into a standard 19-inch computer rack.

  - Matching External Battery cabinets (same size as UPS Enclosures) shall be available in 6, 9 and 12 slot sizes.

  - Dimensions of UPS and Battery Cabinets:

Empty

Enclosure 		Dimensions (H x W x D)		Weights

3 slot			17.8 x 17 x 25.4 inches		66 lbs.

6 slot			31.5 x 17 x 25.4 inches		103 lbs.

9 slot			47 x 24 x 28.4 inches		158 lbs

12 slot			60.7 x 24 x 28.4 inches		196 lbs

2.04   BATTERY

- Battery Type: Valve Regulated Lead Acid (VRLA), minimum 3 year float service life at 25 degrees C.

- UPS Holdover Time (Runtime): Each UPS system, consisting of a minimum of one battery string (consisting of two battery modules) for each power modules shall have a minimum holdover time of 6 minutes.

- Extended Holdover Time (Runtime):  Each UPS system shall have capability for addition of extra matching battery cabinets (in 6, 9 and 12 slot cabinet sizes) to increase the total holdover time.  Please refer to price lists and data sheets for a list of runtimes with 1 to 24 stings of batteries for 3 to 18kVA systems.   The battery times listed are approximate and may vary depending on load configuration and battery charge.

- Battery Recharge Time:

  - Base UPS System consisting of one battery string (two battery modules) for each power module will have a recharge time of 3 hours to 80% usable capacity @ nominal line after a full load discharge.

  - UPS system with more than one battery string (two battery modules) for each power module with have a recharge time calculated by the ampere hour capacity of the total battery system divided by the nominal ampere rating of the battery charger(s) (i.e. 100AH capacity/5 amps of total charge = 20 hours of recharge) after any load discharge.  The New Optional 20 Amp Charger can be used with any UPS system to improve recharge times.

- Bus Voltage: Nominal bus voltage is 120VDC.  This consists of two battery modules, each consisting of (5) 7.2 AH, 12 Volt batteries for a total of (10) 7.2 AH, 12 volt batteries.

- Battery Protection:

  - Short Circuit Protection:  Over-current protection shall protect the batteries from all short circuit and reverse polarity fault conditions.

  - Battery Module Fusing:  Internal Battery Module Fusing shall limit each module to 60 amps.

  - Under-voltage Protection:

    - Inverter cutoff voltage: Battery operation shall be terminated when the battery voltage drops to the load adaptive low battery set point.  At no load the shutdown voltage should be 105VDC.  At full load the terminal voltage of the battery should not go below 95VDC while in Battery Mode.

    - Protective shutdown voltage: System current draw shall be removed from the battery when the battery voltage drops below 1.33 volts-per-cell typical.

  - Over-voltage Protection:  If the UPS systems battery buss voltage exceeds 150VDC for more than 5 seconds the UPS will disable al battery chargers and alarm a high battery condition.

- Battery Management:

  - Battery Recharge:  After recharging batteries to full capacity, the charger will reduce its output to supply internal power supplies only.  Continual float  (trickle) charging of the battery shall not be allowed.  The active battery charger states are Maintenance (no- charge), Constant-Current, and Constant –Voltage (equalize).

  - Battery Runtime Monitoring:  UPS shall monitor batteries and provide status to end user of battery runtime via front panel, serial communications, or both.  Runtime calculations to be based on load demand and analysis of battery health.

  - Battery Health Monitoring: UPS shall periodically monitor battery health and provide warnings visually, audibly and/or serially when battery capacity falls below 80% of original capacity.  Battery testing may also be user initiated via front panel or serial communications.

- External Battery Cabinet Connection: Kit ASY-0525 must be purchased to connect each battery cabinet to the UPS.

- Hot Swappable Battery Modules:  Each Battery Module shall be User-Replaceable and Hot Swappable.  All battery modules shall have a weight of 30lbs or less to insure they are User-Replaceable and Hot Swappable for one person.

- Optional 20 Amp Charger Module:  UPS shall over an optional 20-amp charger (in the same form factor as the 3kVA Power Modules) for use with extended runtime requirements or fast recharge requirements.  This charger shall be Hot Swappable and operational either within the UPS enclosure or within an external battery cabinet with an input connection to utility.

2.05 SYSTEM INPUT & OUTPUT CONNECTIONS

- AC Input:

  - All UPS enclosures shall be capable of utilizing NEMA Input line cords for systems with outputs of less than 9kVA.  NEMA L14-20P, L14-30P and 14-50P can be ordered for 3kVA systems and NEMA 15-50P can be for 6kVA systems.

  - All UPS enclosures shall be capable of utilizing Hardwired Input

  - UPS enclosures with Input Line Cords shall be modifiable (by trained service technicians) to Hardwired Input.

- AC Output:

  - All UPS enclosures shall be capable of utilizing the NEMA receptacles listed below.   The type and quantity of receptacles depends on the UPS enclosure.  For example, a 3 slot UPS Enclosure could be ordered with (4) NEMA 5-15 Duplex receptacles, while a 12 slot UPS Enclosure could be ordered with (16) NEMA 5-15 Duplex receptacles or (8) 3 X NEMA 5-15 Duplex receptacles.

NEMA 5-15 Duplex

NEMA 5-20 Duplex

NEMA 6-15 Duplex

NEMA 6-20 Duplex

NEMA L5-15 Duplex

NEMA L5-20 Simplex

NEMA L5-30 Simplex

NEMA L6-15 Duplex

NEMA L6-20 Simplex

NEMA L6-30 Twist lock Simplex

NEMA L14-20 Twist lock Simples

NEMA L14-30 Twist lock Simplex

3 X NEMA 5-15 Duplex

3 X NEMA 5-20 Duplex

  - All UPS enclosures shall be capable of utilizing Hardwired Output.

  - All UPS enclosures with Receptacles shall be modifiable (by trained service technicians) to Hardwired Output.

- Extended Battery Connector:  Kit ASY-0525 must be purchased to connect each battery cabinet to the UPS.

- Remote Emergency Power Off (EPO) connection:  The UPS shall provide a built-in landing for field connection of a Remote Emergency Power Off circuit.  Upon initiation of the REPO circuit, the UPS shall open its output relays, and disengage the battery converter, preventing power from being delivered to the attached loads.

- Serial (RS-232) Communication Interface: A 9-pin sub-D connector shall provide capability for communicating with manufacture-supplied software package.  The UPS shall also provide signals for indication of AC-Fail; On-Battery and Low-Battery statuses.

- (2) Communication card slots:  The UPS shall provide (2) Communication card slots in the back of the UPS allowing for additional connectivity options, including SNMP/Web capabilities, etc.

- On Generator connection: The UPS shall provide a built-in landing for field connection to a generator.  This connection will aid the UPS in working properly with the generator.

- On Bypass connection:  The UPS shall provide a built-in landing for field connection to a maintenance bypass switch.  This connection will insure the UPS is in bypass mode prior to switching to the maintenance bypass switch.

  - USER INTERFACE

- Front Panel Display:  The UPS shall include a front panel display consisting of a 4 x 20 LCD display, three status LED’s, and a six-key keypad.

  - 4 x 20 LCD display:  Four Language (English, French, German and Spanish), Alphanumeric display of unit function and operating parameters.  It shall be used to signify the operating state of the UPS, for indicating alarms, for changing operations control parameters and set points.

  - Three status LED’s, which indicate:

    - Alarms, with a Red LED

    - On Battery, with a Yellow LED

    - On Utility, with a Green LED

  - Six-Key Multifunction Keypad:  UPS shall have keypad to allow user to adjust UPS parameters, view alarm and inverter logs, change UPS operational modes, turn UPS on and off.

- Power Management Software Package: The UPS shall include serial communications interface that provides the following communication capabilities:

  - Monitor and graphically display input and output voltage and other operating characteristics.

  - Notify end users in the event of a power anomaly via network, E-mail or page

- Communication Ports:

  - (2) Internal Communication Card Slots:  UPS shall have (2) Internal Communication Card Slots for additional communication capabilities, including SNMP/WEB Communication and Dry (Isolated) contact communication.

  - Serial communications (via RS-232) with manufacturer-supplied Power Management Software package.

  - ENVIRONMENTAL CONDITIONS

- The UPS shall be certified to the following safety standards:

  - UL1778 and UL497A

  - CSA22.2 No. 107.1 and 107.2

  - EN50091-1-1

- The UPS shall meet CISPR22 Class A (EN50091-2) for Emissions and EN50091-2 (IEC610003-2 for 16 amps or less) for Harmonics.

- Audible Noise:  Less than 50 dBA (A weighted) at 1 meter from all sides in all system modes.

- Ambient Temperature

  - Operating:  UPS 0 deg C to +40 deg C; battery 20 deg C to 30 deg C for optimum performance.

  - Storage:  UPS -40 deg C to +60 deg C; battery 0 deg C to 32 deg C

E.    Relative Humidity

  - Operating: 5 to 95% non-condensing.

  - Storage: 5 to 95% non-condensing.

F.     Altitude

  - Operating: To 10,000 feet.  Derating or reduced operating temperature range required for higher altitudes.

  - Storage: To 40,000 feet.

- Electrostatic Discharge:  The UPS shall be able to withstand a minimum 15 kV without damage and shall not affect the critical load.

### PART 3 – EXECUTION

3.01 INSTALLATION

- Install in accordance with manufactures instructions and associated User and Installations Manual.