Modbus Profiler Utility - Instructions

V2.10

Powerware Corp.

10/21/2002

1.  Description

Profiler.exe is a Win32 application that reports the availability of Modbus parameters for a particular UPS.  It communicates with the UPS via its native protocol and compares available parameters with a list of possible Modbus parameters for Powerware UPS.  If the parameter in the UPS and parameter in the master list both exist, then the Profiler program reports the supported parameter.

2.  Usage

- Connect the supplied serial cable from the Configuration port on the Modbus Card to an available RS-232 communication port on your computer.

- Copy the profiler.exe, profiler.ini, InputStatus.txt, and InputRegisters.txt files from the supplied Powerware diskette to your PC.

- From the command prompt, run profiler comX 9600, where X is the communication port number on your PC and 9600 is the baud rate for communication with the UPS.

Alternately, if you run profiler (without the parameters), it defaults to COM1 and 9600 baud through a reference to the parameters in the profiler.ini file.

- Profiler creates an output file named profiler.csv in the directory where the Profiler tool is located.

Before the program exists, you are prompted to view the data.

The comma-delimited file can be easily imported into Microsoft Excel for viewing of the Modbus data. This data is used to create the necessary template files on your Building Management System Software for polling the desired UPS information.