INSTALL CONDUIT SYSTEMS

Subcourse Number EN 5143

### EDITION B

United States Army Engineer School

Fort Leonard Wood, Missouri  65473

8 Credit Hours

Edition Date:  April 2000

### SUBCOURSE OVERVIEW

This subcourse is designed to teach the knowledge necessary to classify and size, cut and thread, and bend and install conduit and install conductors.

There are no prerequisites for this subcourse.

This subcourse reflects the doctrine which was current at the time it was prepared.  In your own work situation, always refer to the latest official publications.

Unless otherwise stated, the masculine gender of singular pronouns is used to refer to both men and women.

## TERMINAL LEARNING OBJECTIVE:

ACTION:	You will learn the different types and sizes of conduit and how to cut, thread, bend, and install it; to use calculations; and to install conductors.

CONDITION:	You will be given the material in this subcourse and an Army Correspondence Course Program (ACCP) examination response sheet.

STANDARD:	To demonstrate competency of this task, you must achieve a minimum of 70 percent on the subcourse examination.

TABLE OF CONTENTS

#### Section											Page

Subcourse Overview	i

Administrative Instructions	iv

Grading and Certification Instructions	iv

Lesson 1:  Classifying and Sizing Conduit	1-1

Part A:  Rigid Steel Conduit	1-1

Part B:  EMT Conduit	1-2

Part C:  Rigid Nonmetallic (PVC) Conduit 	1-2

Part D:  Flexible Metallic and Nonmetallic Conduit 	1-3

Practice Exercise	1-5

Answer Key and Feedback	1-6

Lesson 2:  Cutting and Threading Conduit	2-1

Part A:  Cutting Conduit 	2-1

Part B:  Threading Conduit 	2-4

Practice Exercise	2-7

Answer Key and Feedback	2-8

Lesson 3:  Bending Conduit	3-1

Part A:  Methods of Bending Conduit	3-1

Part B:  Types of Bends 	3-2

Part C:  Types of Benders 	3-9

Practice Exercise	3-13

Answer Key and Feedback	3-14

Lesson 4:  Installing Conduit and Conductors	4-1

Part A:  Installing Conduit 	4-1

Part B:  Installing Conductors 	4-8

Practice Exercise	4-11

Answer Key and Feedback	4-12

Examination	E-1

Appendix A: Metric Conversion Chart 	A-1

Appendix B:  List of Common Acronyms	B-1

Appendix C:  Recommended Reading List	C-1

Student Inquiry Sheets

ADMINISTRATIVE INSTRUCTIONS

1.  Number of lessons in this subcourse:  Four.

2.  Materials you need in addition to this booklet are a number 2 pencil and the ACCP examination response sheet with the preaddressed envelope you received with this subcourse.

3.  Supervisory requirements:  None.

4.   References:  The following publication provides additional information about the material in this subcourse.  You do not need this material to complete this subcourse.

- Soldier Training Publication (STP) 5-51R12-SM-TG.  Soldier's Manual and Trainer's Guide, MOS 51R, Interior Electrician, Skill Levels 1/2.  27 October 1988.

- FM 5-424.  Theater of Operations Electrical Systems.  25 June 1997.

- 1999 National Electrical Code( (NEC(), available from the (

National Fire Protection Association

1 Batterymarch Park

Quincy, Massachusetts 02269-9101

##### GRADING AND CERTIFICATION INSTRUCTIONS

Examination:  This subcourse contains a multiple-choice examination covering the material in the four lessons.  After studying the lessons and working the practice exercises, complete the examination.  Mark your answers in the subcourse booklet, then transfer them to the ACCP examination response sheet.  Completely black out the lettered oval that corresponds to your selection (A, B, C, or D).  Use a number 2 lead pencil to mark your responses.  When you complete the ACCP examination response sheet, mail it in the preaddressed envelope you received with this subcourse.  You will receive an examination score in the mail.  You will receive eight credit hours for successful completion of this examination.

LESSON 1

CLASSIFYING AND SIZING CONDUIT

Critical Task:  051-246-1114

OVERVIEW

LESSON DESCRIPTION:

In this lesson, you will learn some of the different types and sizes of conduit used in electrical work.

# TERMINAL LEARNING OBJECTIVE

ACTION:		You will learn the different types and sizes of conduit.

CONDITION:		You will be given the material contained in this lesson.

STANDARD:		You will correctly answer practice-exercise questions at the end of this lesson.

REFERENCES:	The material contained in this lesson was derived from FM 5-424 and NEC.

INTRODUCTION

Conduit is a rugged, protective tube through which wires are pulled.  Careful planning and practice will result in a professional-looking electrical system.  A conduit wiring system is probably the most challenging of the electrical systems to install.

Although several types of conduit are used in electrical work, only the following types will be discussed in this subcourse: rigid-steel, electrical metallic tubing (EMT), rigid non-metallic (polyvinyl chloride [PVC]), and flexible metallic and nonmetallic conduit.

## PART A:  RIGID-STEEL CONDUIT

Rigid-steel conduit is a heavy-duty pipe that is similar in appearance to metal water pipe.  It is threaded at both ends.  Rigid-steel conduit provides the best protection from physical abuse because of its strength.   Article 349 in the NEC covers rigid-steel conduit (Figure 1-1, page 1-2).

Figure 1-1.  Rigid-steel conduit

The size of rigid-steel conduit is the inside-diameter measurement.  Rigid-steel conduit is available in sizes from 1/2 inch to 6 inches.  These sizes will accommodate any job.  A breakdown of the sizes of rigid-steel conduit in inches follows:  1/2, 3/4, 1, 1 1/2, 2, 2 1/2, 3, 3 1/2, 4, 5, and 6.

A full-length piece or stick of rigid-steel conduit is 10 feet long.  Galvanized-steel conduit is available for application in wet areas or underground.  Galvanizing prevents the rusting of conduit from moisture.

PART B:  EMT CONDUIT

EMT conduit is a light-gauge pipe often referred to as thin-wall conduit (Figure 1-2).  The wall thickness of EMT conduit is about 40 percent less than that of rigid-steel conduit, and because of the thickness of EMT conduit, it can be easily bent.  Article 348 in the NEC covers EMT conduit.

Figure 1-2.  EMT (thin-wall) conduit

EMT conduit is available in inside diameters ranging from 1/2 inch to 4 inches.  Like rigid-steel conduit, EMT conduit comes in 10-foot lengths.  A breakdown of the sizes of EMT conduit in inches follows:  1/2, 3/4, 1, 1 1/2, 2, 2 1/2, 3, 3 1/2, and 4.

PART C:  RIGID NONMETALLIC (PVC) CONDUIT

PVC conduit is produced and used for below-ground (direct burial or concrete encasement) installation.  It provides high strength, a low absorption rate, watertight joints, and low installation costs.  It is available in inside diameters ranging from 1/2 inch to 5 inches.  PVC conduit comes in lengths of up to 20 feet (Figure 1-3).  Article 347 in the NEC covers PVC conduit.

Figure 1-3.  PVC conduit

A breakdown of the sizes of PVC conduit in inches follows:  1/2, 3/4, 1, 1 1/4, 1 1/2, 2, 2 1/2, 3, 3 1/2, 4, and 5.

PART D:  FLEXIBLE METALLIC AND NONMETALLIC CONDUIT

Flexible metallic conduit (Figure 1-4) is similar in appearance to metallic armored cable, but they are unlike them because flexible metallic conduit is not preinstalled with conductors. In flexible metallic conduit, conductors must be pulled through the conduit after it is installed.  Flexible metallic conduit is generally used where some type of movement or vibration may be present, such as wiring motors.  Article 350 in the NEC covers flexible metallic conduit.

Figure 1-4.  Flexible metallic conduit

Flexible metallic conduit comes in two types, aluminum and steel.  The available size of flexible metallic conduit depends on the type.  The sizes may vary depending on the manufacturer.  The NEC states that flexible metallic conduit will not be smaller than 3/8 inch and not larger than 4 inches (Table 1-1, page 1-4).  Flexible metallic and nonmetallic conduit is available for use in wet areas.

Table 1-1.  Flexible metallic conduit sizes

| Steel (Inches) | Aluminum (Inches) |
| --- | --- |
| 3/8 | 3/8 |
| 1/2 | 1/2 |
| 3/4 | 3/4 |
| 1 | 1 |
| 1 1/4 | 1 1/4 |
| 1 1/2 | 1 1/2 |
| 2 | 2 |
| 2 1/2 | 2 1/2 |
| 3 | 3 |
|  | 3 1/2 |
|  | 4 |

LESSON 1

PRACTICE EXERCISE

The following items will test your grasp of the material covered in this lesson.  There is only one correct answer for each item.  When you complete the exercise, check your answers with the answer key that follows.  If you answer any item incorrectly, study again that part of the lesson which contains the information involved.

1.  Which of the following types of conduit provides the best protection from physical abuse?

A.  Flexible

B.  EMT

C.  Rigid steel

D.  PVC

2.  How can rusting of steel conduit be prevented when underground installation is necessary?

____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

LESSON 1

PRACTICE EXERCISE

ANSWER KEY AND FEEDBACK

Item		Correct Answer and Feedback

1.		C.  	Rigid-steel conduit provides the best protection from physical abuse…(page 1-1, para 3)

2.			Galvanized-steel conduit is available for application in wet areas or underground.  Galvanizing prevents the rusting….(page 1-2, para 2)

# LESSON 2

# CUTTING AND THREADING CONDUIT

# Critical Task:  051-246-1114

# OVERVIEW

# LESSON DESCRIPTION:

In this lesson, you will learn the methods on how to cut and thread conduit so that connections can be made electrically secure and mechanically tight.

# TERMINAL LEARNING OBJECTIVE:

ACTION:		You will learn the methods on how to cut and thread conduit.

CONDITION:		You will be given the material contained in this lesson.

STANDARD:		You will correctly answer practice-exercise questions at the end of this lesson.

REFERENCES:	The material contained in this lesson was derived from FM 5-424 and NEC.

# INTRODUCTION

Although it may seem at first glance to be a simple task, cutting and threading conduit efficiently requires considerable skill.  With the instructions that follow and on-the-job experience, you should soon be able to do this well.

# PART A:  CUTTING CONDUIT

Regardless of the type of conduit being installed, you will often have to cut it to make it fit. All conduits should be cut at a 90( angle.  Rigid-steel conduit can be cut with either a hacksaw or a pipe cutter.  Although a vise is not absolutely necessary, it makes cutting with either tool much easier (Figure 2-1, page 2-2).

# Figure 2-1.  Cutting and reaming tools

When cutting any conduit with a hacksaw, use a blade with 18 to 32 teeth per inch.  A blade with fewer teeth hangs up, binds, or even breaks (Figure 2-2).  Put the blade in the hacksaw frame (with the teeth pointing forward) so that the teeth cut when you push the saw forward.  Place the pipe in the vise so that there  is ample room between the vise and the cut.  This lets you saw without hitting your hands on the vise and allows enough room for threading purposes after the cut is made.  Remember, let the saw work for you, do not force it.  Use a steady forward cutting stroke with light to medium pressure.

Figure 2-2.  Hacksaw blades

To use a pipe cutter, place the conduit in the vise as described above for cutting with a hacksaw.  Put the cutter over the conduit and adjust it until the cutting wheel makes contact at the point of the cut (Figure 2-3).

# Figure 2-3.  Pipe cutter

Tighten the cutter just enough to score the pipe on the first turn.  Then, screw the handle in about one-fourth of a turn for each turn around the conduit until the cut is complete.  Cutting oil can be used to ease the cutting action.  Rigid-steel conduit is cut the same way.

EMT and PVC conduit should be cut with a hacksaw because pipe cutters may flatten the end of the pipe.  Pipe cutters also leave a ridge on the inside of the pipe that is very hard to remove.  There are tubing cutters made specifically for cutting EMT or PVC (Figure 2-4), but be sure you have the correct cutter for the job.  As stated before, when cutting conduit with a hacksaw or tubing cutter, using the vise will make the job much easier.  The tubing cutter is used the same way as the pipe cutter.

Figure 2-4.  Tubing cutter

Flexible metallic and nonmetallic conduit should also be cut with a hacksaw at a 90( angle. Cutting any type of conduit leaves a sharp edge or burrs on the inside of it that must be removed by reaming.

To ream rigid-steel conduit, use the reamer shown in Figure 2-5, page 2-4. A rat-tail file does a good job on any type of conduit.  Use pliers, such as needle-nose or side-cutting pliers, to ream EMT that has been cut with a hacksaw.  The important thing is to remove any sharp edge or burrs inside the conduit that might cut the insulation when the conductors are pulled into it.

# Figure 2-5.  Reaming tools

## PART B:  THREADING CONDUIT

Once rigid-steel conduit is cut, it must be threaded for use with threaded couplings, locknuts, and bushings.  To thread conduit, use a pipe-cutting die with a standard pipe thread of 3/4-inch taper per foot.  This die cuts a deeper thread on the end of the conduit and then tapers the cut at the rear or shoulder of the thread.  This is just the opposite of a running thread on a bolt.

The dies used for threading smaller sizes of conduit are usually hand-driven (Figure 2-6).  The handle may be solidly attached to the die, or the die assembly may be a ratchet-type.  When using larger sizes or installing large amounts of conduit that require considerable threading, a motor-driven, pipe-threading machine is recommended.

# Figure 2-6.  Nonadjustable ratchet and dies

The most common rigid-steel conduit threader is a nonadjustable ratchet and dies, which come in sizes to fit conduit from 1/2 inch to 2 inches (Figure 2-6).

Before threading the conduit, inspect the dies to see that they are sharp and free from nicks and wear.  Next, insert the conduit into the vise, place the guide end of the pipe threader on the conduit, and push the threading dies against the conduit with the heel of your hand (Figure 2-7).

# Figure 2-7.  Threading conduit

With pressure against the threader, take three or four short, clockwise strokes downward to start the threads.  Continue the threading with clockwise strokes, mixed with a reverse stroke every now and then, until two or three threads extend beyond the die.  To reverse the threader, pull the ratchet lock out and turn it a half turn.  The reverse turns keep the threads and dies clean and free of bits of metal.  Cutting oil applied during the threading helps the cutting process by reducing friction.  To remove the threader, release the ratchet lock and turn the die by hand counterclockwise.  Removal of the die also cleans the threads.

It is important that the right amount of threads be cut for the job.  In other words, a full thread must be cut so that the ends of the conduit come together in the coupling (Figure

2-8).

Figure 2-8.  Threaded coupling

Full threads are also necessary for the conduit to make a firm seat in the end threads of the hub.  Cutting threads until two or three threads extend beyond the die usually gives you a full thread. However, if too many threads are cut, the conduit will fit too loosely in the coupling or against the hub.

Power threaders come in the following two types: stationary threaders built for use in the shop and portable threaders built for use in the field.  Both types are driven by electric motors that have adjustable chucks and dies for use on different sizes of conduit.  Portable threaders normally handle conduit up to 2 inches.  Shop threaders may be built to handle conduit up to 6 inches.  Consult the manufacturer's operating instructions before using these power tools.

# LESSON 2

# PRACTICE EXERCISE

The following items will test your grasp of the material covered in this part of the lesson.  There is only one correct answer for each item.  When you complete the exercise, check your answer with the answer key that follows.  If you answer any item incorrectly, study again that part of the lesson which contains the portion involved.

# 1.  How many teeth per inch should a hacksaw blade have for cutting conduit?

# A.  10-15

B.  14-20

C.  16-24

D.  18-32

# 2.  What is the taper in inches per foot for a standard pipe-cutting die?

# A.  3/4

B.  1

C.  1 1/4

D.  1 1/2

# LESSON 2

# PRACTICE EXERCISE

# ANSWER KEY AND FEEDBACK

Item			Correct Answer and Feedback

1.			D.  	When cutting any conduit with a hacksaw, use a blade with

18 to 32 teeth per inch.  (page 2-2, para 1)

2.			A.  	To thread conduit, use a pipe-cutting die with a standard pipe thread of 3/4-inch taper per foot.  (page 2-4, para 2)

LESSON 3

###### BENDING CONDUIT

Critical Task:  051-246-1114

OVERVIEW

LESSON DESCRIPTION:

In this lesson, you will learn how to use calculations and make bends in conduit.

TERMINAL LEARNING OBJECTIVE:

ACTION:		You will learn how to use calculations and make bends in conduit.

CONDITION:		You will be given the material contained in this lesson.

STANDARD:		You will correctly answer all practice-exercise questions at the end of this lesson.

REFERENCES:	The material contained in this lesson was derived from FM 5-424 and NEC.

INTRODUCTION

One of the tasks you will have as an electrician is to make field bends in conduit.  Although conduit bending is thought by many electricians to be difficult, it is fairly simple.  It does require some thought, simple math calculations, and a lot of practice.

##### PART A:  METHODS OF BENDING CONDUIT

When you are installing conduit, you will need to make bends to go over or around obstacles.  These bends must be made without reducing the inside diameter of the conduit at the bend.  You will make most bends on the job as a part of the installation procedure.  These are called field bends.  Factory-made bends may be used instead of field bends; however, they increase the cost of the job because they are an added cost and may require more cutting, threading, and bending.

Since most of the bending you do will be done with manual benders, the bending procedures taught will be made with those types of tools.  There are basically two types of manual benders used for bending rigid-steel conduit and EMT.  They are the rigid bender, called the hickeys, and the EMT bender.  The EMT bender is normally made for EMT, but some are made to be used for both EMT and rigid-steel conduit.  The EMT bender is capable of making a full 90( bend with a single motion.  Conduit sizes up to 1 inch for rigid steel and 1 1/4 inch for EMT can be bent using manual benders.  Larger sizes are usually bent with power benders (Figure 3-1).

Figure 3-1.  Benders

PART B:  TYPES OF BENDS

Conduit installations are normally referred to as runs of conduit.  A run of conduit is the conduit, fittings, straps, conductors, and bends needed from one opening to the next (for example, from the panel board to the first outlet box or from the first outlet box to the second outlet box).  In a run of conduit, there cannot be more than the equivalent of four 90( bends, for a total of 360(.  The purpose of allowing only so many bends in a run of conduit is to help in pulling conductors into the conduit.  Experience has taught that if more than 360( of bends are used, it is very difficult to pull conductors through the bends (Figure 3-2).

### Figure 3-2.  360( bend

Conduit bodies are available in the following configurations: elbow back (LB), elbow right (LR), elbow left (LL) and a T.  The configuration of each is determined based on the location of the removable cover (Figure 3-3).

Figure 3-3.  Conduit bodies

By using a conduit body in a run, you provide an opening for pulling the conductors without having to mount a box.  At the same time, you can make a turnaround or go over an obstacle and maintain a neat conduit installation.  The turn or 90( turn made by the conduit body does not count as one of the four allowable bends in a run.  As a matter of fact the conduit body is identified as an outlet box.

One of the most common bends you will make in the field is the right-angle bend, more commonly called a 90( bend or just a 90.  It can be used for going around an inside corner, into the top or bottom of a box from a horizontal run, or over an object.

Anyone can make a 90( bend in a stick of conduit and then cut it off to make it fit the situation, but this practice wastes time and material.  The secret is to find out where the bend is needed, mark the conduit accordingly, and make the bend in the right place.  This practice saves time and material.  Before you can determine where to place your bender on the conduit, there are some things you must know.  First, there are two lengths on the conduit that must be considered, from one end of the conduit to the 90( bend and then from the 90( bend to the other end of the conduit.  The shorter of these two lengths is called the stub end, or simply the stub (Figure 3-4A), and the longer is the running end.  Second, the radius of the bend takes up a part of the stub.  This part of the stub is called take-up and is shown in Figure 3-4B.  The amount of take-up depends on the type and size of the conduit you are bending (Table 3-1).

Figure 3-4.  Conduit bending terms

### Table 3-1.  Conduit take-up

| Amount of Take-Up for 90( Bends Using an EMT Bender |
| --- |
| Size and Type of Conduit | Take-Up |
| 1/2-inch EMT 3/4-inch EMT or 1/2-inch rigid steel* 1-inch EMT or 3/4-inch rigid steel* 1 1/4-inch EMT or 1-inch rigid steel* | 6 inches 6 inches 8 inches 11 inches |

In the following example, you are going to make a 90( bend using 1/2-inch EMT conduit and the EMT bender.  You are going to run the conduit from the top of a panel to the ceiling and then horizontally along the ceiling.  Measure from the top of the panel to the ceiling.  This will give you the stub length of 18 inches.  Measure 18 inches from the end of the conduit and make a mark (Figure 3-4).

Look at Table 3-1 to find out what the take-up is for 1/2-inch EMT conduit.  The take-up is 6 inches.  Measure back 6 inches from the first mark toward the end of the conduit and make a second mark as shown in Figure 3-5.

Figure 3-5.  Placing the bender to make a 90( bend

Hold the bender in one hand with the lip on the floor pointed toward the stub end.  Use the other hand to place the conduit in the bender.  Align the bender arrow with the take-up mark.  Put one foot on the footrest and hold the handle with both hands.  To make the bend, apply pressure on the footrest as you pull on the handle until the handle is parallel with the floor.  It is OK to go slightly beyond 90( with the bend, in fact it is preferred, because it is easy to bring it back to 90(.

You should now have a 90( bend with an 18-inch stub  (Figure 3-6).  To see whether the bend will fit properly, place it next to something that has a right angle (for example, in the corner where the floor and wall meet).

Figure 3-6.  90( bend with an 18-inch stub

If the bend is more than 90(, you can stand on the running end and push out on the stub end, a little at a time, until it is 90(.  If the stub is too short or if the conduit is too long to push back, place the handle of the bender over the end of the stub and, with one foot on the conduit on the floor, spring the stub back (right-angle bends should always be made with the conduit and the bender on the floor).

In this example, you are going to make a 90( bend in the conduit and run it along the wall. The first thing you must do is establish a reference point using the following steps:

Step 1.  Measure the distance from the outside edge of the knockout to the wall at box A (Figure 3-7).

Step 2.  Transfer that measurement above box A and across from box B. Mark a reference line (Figure 3-7).

Step 3.  Measure the distance from the outside edge of the knockout to the ceiling at box B (Figure 3-7).

Step 4.  Transfer that measurement across from box B and above box A. Mark a reference line.  Where the two lines cross is the reference point (Figure 3-7).

Figure 3-7.  90( bend

NOTE: Conduit will not go completely to a reference point and make a 90º turn.  If it did, the inside diameter would be decreased and the conduit would be creased.  Since the conduit is not going all the way to the reference point, you will gain distance on the conduit.  In Table 3-2, the “bender gain” for making 90º bends in conduit is shown.

Step 5.  Measure from box A to the reference point and add this measurement to the measurement between box B and the reference point.  Deduct the gain (Table 3-2).  This will give you the length for the piece of conduit you need to run between boxes A and B (Figure 3-7).

### Table 3-2.  Bender gain table

| Size of Conduit | 90( Gain |
| --- | --- |
| 1/2-inch EMT | 2 5/8 inches |
| 3/4-inch EMT – 1/2-inch rigid steel | 3 1/4 inches |
| 1-inch EMT – 3/4-inch rigid steel | 4 inches |
| 1 1/4-inch EMT – 1-inch rigid steel | 5 5/8 inches |

NOTE: When taking measurement for the length of conduit, measure from the box itself, not from the box connector.

In the following example, you are going to run 1/2-inch EMT from box “A” to box “B.”  The measurement from box “A” to the reference point is 15 inches and from box “B” to the reference point is 30 inches.  Add the two measurements together to get the total length of 45 inches.  Deduct the  “bender gain,” which is 2 5/8 inches.

With this information, you know that you must subtract the “gain” so that the conduit will not be too long (45 inches – 2 5/8 inches = 42 3/8 inches).  Cut a piece of conduit 42 3/8 inches long to go from box “A” to box “B.”  After the EMT is cut and reamed, the next thing to do is bend offsets and then a 90 in the conduit.

An offset bend is two equal bends in opposite directions.  It is used to avoid contacting a part of the structure or to bring the conduit out from the structure to match a knockout in a box or panel.

Figure 3-8 shows an offset into a utility box.  The angle of the bends in an offset depends on several things:  the amount of offset that is needed, the amount of room there is where the offset is going to be placed, and the type of obstacle you are avoiding.  The offset shown is usually about 1/2 inch deep, and the bends are about 8º angles.  Often, these bends will need to be made on both ends of the conduit to enter two boxes.  To make this type of offset, make a mark on each end of the conduit 1 1/2 inches from the ends.  Make another mark at each end 4 1/2 inches from the end.  Place the conduit in the bender on the 1 1/2-inch mark and make an 8º angle bend on both ends.  Turn the bender over and make bends on the 4 1/2-inch marks with the bender head in the air.  Once the bends are made, check them by placing the conduit on a flat surface and putting a tape measure behind the conduit and measuring the distance from the bottom of the conduit to the flat surface.  If you do not have a 1/2-inch offset, place the conduit back in the bender with the bender head in the air and make adjustments until you have a 1/2-inch offset.  The key to making a good box offset is practice.  Notice that after the bends are made, the conduit sections on each end of the offset are parallel to each other.

Figure 3-8.  Offset in a utility box

Table 3-3 is a guide for offsets.  The following example shows how to figure offsets.  For example, if a 3-inch offset is needed, the distance between the bends would be 6 inches(if the first mark was 2 inches from the end of the conduit, the second mark would be at 8 inches from the end of the conduit.  The angle of bend would be 30º and the conduit length loss would be 3/4 inch; therefore, the conduit should be 3/4 inch longer to make up for the loss (Figure 3-9).

Table 3-3.  Guide for offsets

| Offset Depth | Distance Between Bends | Angle of Bends | Conduit Shortens |
| --- | --- | --- | --- |
| 1 inch | 6 inches | 10 º | 1/16 inch |
| 2 inches | 5 1/4 inches | 22 1/2º | 3/8 inch |
| 3 inches | 6 inches | 30º | 3/4 inch |
| 4 inches | 8 inches | 30º | 1 inch |
| 5 inches | 7 inches | 45º | 1 7/8 inch |
| 6 inches | 8 1/2 inches | 45º | 2 1/4 inches |
| 7 inches | 9 3/4 inches | 45º | 2 5/8 inches |
| 8 inches | 11 1/4 inches | 45º | 3 inches |
| 9 inches | 12 1/2 inches | 45º | 3 3/8 inches |
| 10 inches | 14 inches | 45º | 3 3/4 inches |

### Figure 3-9.  3-inch offset

Table 3-4 shows an offset formula to use.  The following paragraphs explain how to use this table.  Multiply the offset angle and the multiplier to find the distance between the offsets.  The angle that you use depends on how much room there is on your site to run the conduit. For example, if you need a 5-inch offset and use a 30º angle; the constant multiplier would be 2 (5 X 2 = 10).  The distance between the bends would be 10 inches.  The conduit length loss will be 1/4 inch of conduit  for every inch of offset; therefore, add 1 1/4 inch of conduit to the length.

Table 3-4.  Offset formula

| Angle of offset | Multiplier | Conduct Length Loss per Inch of Depth |
| --- | --- | --- |
| 10º | 6 | 1/16 inch |
| 22 1/2º | 2.6 | 3/16 inch |
| 30º | 2 | 1/4 inch |
| 45º | 1.4 | 3/8 inch |
| 60º | 1.2 | 1/2 inch |

Place the marks for the bends 10 inches apart.  Using the arrow of the bender, make a 30º bend on the same side of each mark (Figure 3-9).  A 30º bend will give you the offset you need.  If you make both bends inside the marks, you will end up with much less than the desired offset.  If you make both bends outside the marks, you will have too much offset.  The amount of bend is obtained by using the degree markings on the bender.  Once the bends have been made, verify the offset depth by placing it on a flat surface and measuring the distance from the bottom of the conduit to the flat surface.

The back-to-back bend is actually two adjacent 90( bends made in the same piece of conduit.  Make the first 90( bend with a certain amount of stub as described previously.  To determine where to place the bender for the second bend, you must first have an outside-to-outside measurement.  This measurement is the distance from the back of the first bend to where you want the back of the second bend.  You must then transfer this measurement to the conduit and make a mark.  The easiest way to make a back-to-back bend is to turn the bender around, line up the star of the bender with your outside-to-outside measurement, and pull the bend in the opposite direction (Figure 3-10).

Figure 3-10.  Back-to-back bend

# PART C:  TYPES OF BENDERS

The procedures for making the different types of bends discussed this far have all been with an EMT bender.  The same bends can be made with a hickey bender, although the procedures are slightly different.  For instance, to make a 90º bend in 1/2-inch rigid-steel conduit, several steps must be used (Figure 3-11).

Figure 3-11.  Making a 90( bend with a hickey bender

In the following example, you are going to make a 90( bend with a 20-inch stub in 1/2-inch rigid-steel conduit.  The steps for making a bend with a hickey bender are as follows:

Step 1.  Make a mark 20 inches from the end of the conduit.

Step 2.  Determine the take-up for 1/2-inch rigid-steel conduit (Table 3-1, page 3-4).

Step 3.  Make a second mark 6 inches back from the first mark toward the end of the

conduit.

Step 4.  Place the bender at the second mark and make about a 30º bend.

Step 5.  Move the bender toward the 20-inch mark (about 2 inches).  Make another 30º

bend.

Step 6.  Move the bender to where the heel of the bender is on the 20-inch mark and

complete the 90º bend.

Since the hickey bender does not usually have degree markings on it, you must estimate the amount of bend you are making with each bite.  Small bites reduce the possibility of crimping or kinking the conduit.

Power benders are used for bending larger sizes of EMT and rigid-steel conduit.  They are also used where many bends must be made, regardless of the size of the conduit.  They come in many types and sizes.  The most common power bender is hydraulic.  It is used to bend all types of bendable conduit.  Hydraulic benders use either a hand pump or an electric pump to move a shoe that does the actual bending.

Figure 3-1, page 3-2, shows a hydraulic sweep bender that uses a hand pump.  By using different-size bending dies at different locations on the tie bar, the bender can be used to bend several types and sizes of conduit.  The procedures for making the different types of bends with power benders are very similar to those used with manual benders.  The main difference is that with power benders the take-up for 90º bends and the distance between the bends for offsets will not be the same as those shown in Table 3-1, page 3-4 and Table 3-3, page 3-8.  This is due to the fact that you are dealing with larger sizes of conduit or the shoes of the bender give a different radius of bend.  Because there are so many different types and manufacturers of benders, be sure to check the manufacturer's instructions before making any bends.

PVC is used primarily in underground or permanently wet locations and must have a separate equipment grounding conduct installed.  Allowance must be made for this conductor when the maximum number of conductors permitted by the NEC is calculated.

PVC elbows and offset fittings are available for standard bends.  For other bends, a special device called a hotbox must be used.  The hotbox electrically heats the PVC and softens it so that it can be bent to the desired shape (Figure 3-12).  Before heating the PVC section (especially sizes 2 inches and larger), plug both ends.  This traps air in the conduit.  The air, heated in the hotbed, expands to prevent kinks or dislocation of the conduit when it is bent.

### Figure 3-12.  Hotbox

PVC is durable, easy to work with, and moderate in cost.  It is particularly well suited to areas where resistance to moisture and corrosion is essential.  The main disadvantage of PVC is that joints cannot be taken apart after they are cemented.

# LESSON 3

# PRACTICE EXERCISE

The following items will test your grasp of the material covered in this part of the lesson.  There is only one correct answer for each item.  When you complete the exercise, check your answers with the answer key that follows.  If you answer any item incorrectly, study again that part of the lesson which contains the portion involved.

1.  Which manual bender is used to make a full 90º bend with one motion?

A.  hickey.

B.  EMT bender.

C.  hotbox.

D.  hydraulic.

2.  What is the maximum number of 90º bends that can be made in a run of conduit?

A.  1

B.  2

C.  3

D.  4

LESSON 3

PRACTICE EXERCISE

ANSWER KEY AND FEEDBACK

Item		Correct Answer and Feedback

1.  		B.  	The EMT bender is capable of making a full 90º bend with a single motion.  (page 3-2, para 1)

2.		D.  	In a run of conduit, there cannot be more than the equivalent of four 90º bends, for a total of 360º.  (3-2, para 2)

LESSON 4

INSTALLING CONDUIT AND CONDUCTORS

Critical Task:  051-246-1114

OVERVIEW

LESSON DESCRIPTION:

In this lesson, you will learn how to install conduit and conductors as per construction prints and the NEC.

TERMINAL LEARNING OBJECTIVE:

ACTION:		You will learn how to install conduit and conductors as per construction prints and the NEC.

CONDITION:		You will be given the material contained in this lesson.

STANDARD:		You will correctly answer all practice-exercise questions at the end of this lesson.

REFERENCES:	The material contained in this lesson was derived from FM 5-424 and NEC.

INTRODUCTION

In this lesson, the specific requirements for installing conduit and conductors will be discussed.

PART A:  INSTALLING CONDUIT

Several general requirements apply to all types of conduit installation.  All runs must be installed as a complete system before any conductors are pulled into them.  In other words, a run of conduit (to include conduit, fittings, and supports) must be complete before the conductors are installed.  A run of conduit should be as straight and direct as possible.  When a number of conduit runs are to be installed parallel and next to each other, install them all at the same time.  The minimum size raceway that can be installed is generally 1/2-inch electrical trade size.  There are exceptions to this rule depending on specific locations.  The exceptions for each type are outlined in the NEC.

All types of conduit must be reamed after they have been cut.  Conduit threaded in the field must be threaded with a die that has a 3/4-inch taper per foot.  Also, never use threaded couplings with running threads.  Running threads weaken the conduit and may come loose. Threaded couplings and connectors used with any type of conduit must be made with tight connections.  When the couplings or connectors are to be buried in concrete or masonry they must be the concrete-tight type.  When installed in wet locations, they must be the watertight type.

Fittings for EMT are of two general types(watertight fittings that may be used outdoors or in any location and fittings that provide strong mechanical and electrical connections, but may be used only in dry locations.

The watertight fittings join sections of tubing by means of a five-piece compression fitting.  (Figure 4-1).

Figure 4-1.  Five-piece compression fitting

To put a watertight fitting together, use the following steps:

Step 1.  Place a gland nut and compression ring over the end of each piece of tubing (in that order).

Step 2.  Slip a double-threaded ring (called the body) over the end of each section.

Step 3.  Screw the gland nuts onto the body and tighten them to squeeze the

compression rings.  The rings form a watertight seal.

A similar fitting having only three pieces is used to make a watertight joint to metal boxes (Figure 4-2).

### Figure 4-2.  Three-piece fitting

To make a watertight joint to a metal box, use the following steps:

Step 1.  Place the large nut and compression ring on the end of the EMT.

Step 2.  Place the double-threaded body over the end.

Step 3.  Screw the nut onto the body to squeeze the compression ring and make a

watertight seal.

Step 4.  Use the exposed threads on the body to secure the EMT to a weatherproof box

using a locknut and bushing (Figure 4-3).

### Figure 4-3.  Opened three-piece fitting

Fittings for use in dry locations are simpler to use and less expensive.  One type consists of a sleeve and two or four setscrews (Figure 4-4).

### Figure 4-4.  Dry-locations fittings

Another form of coupling is made by using a plain sleeve and an indenting tool (Figure

4-5).

### Figure 4-5.  Plain sleeve and indenting tool coupling

To put on an indented coupling, use the following steps:

Step 1.  Place the sleeve over the ends to be joined.

Step 2.  Use the indenting tool to make indents in the coupling and the tubing to secure 	the joint.  The tool makes two indents at once on either side of the coupling (Figure 4-6).

### Figure 4-6.  Indenting tool

Step 3.  Use the tool twice, 1/4 turn apart, on each end of the coupling, to make a total

weight of eight indents at the joint.

Fittings used for rigid-steel and PVC conduit are similar to those used for EMT.  Threaded and threadless couplings and connectors are available for use with rigid-steel and PVC conduit and PVC.  The threadless fittings are installed in the same way as those for EMT.  The advantage of using threadless couplings and connectors is that threading the conduit is not required.  Because EMT has a thin wall, it cannot be threaded, thus threaded couplings cannot be used with EMT (Figure 4-7).

### Figure 4-7.  Threadless couplings and connectors

On rigid steel conduit threaded couplings are screwed onto the threaded ends of the conduit and tightened with a pipe wrench (Figure 4-8).

### Figure 4-8.  Threaded coupling

Rigid-steel and PVC conduit is connected to electrical boxes by locknuts (Figure 4-9).  The locknuts are tightened against each side of the box wall.  The bushing is placed over the end of the conduit to provide the conductor with protection from physical damage.

Figure 4-9.  Box connector

Fittings for flexible metallic conduit are either internally or externally attached to the conduit.  The internal type is designed to screw into the spiral of the conduit.  This type of connector covers the end of the conduit completely, protecting the conductors from contact with the cut edge of the conduit.  Externally attached connectors are secured to the conduit with clamping screws (Figure 4-10).

Figure 4-10.  Flexible metallic conduit connector

When using these connectors, make sure that the cut end of the conduit is pushed as far as possible into the connector, covering the cut end and protecting the conductors from damage.

NOTE:  The spiral construction of flexible metallic conduit causes it to have a higher electrical resistance per foot than solid metallic conduit.  For this reason, flexible metallic conduit should not be used as a grounding conductor.  An additional bare or green-insulated grounding conductor should be included with the current-carrying conductors in flexible conduit installations.

A special type of metallic flexible metallic conduit is made for use in wet areas.  It is called liquid-tight.  Liquid-tight fittings are available for use with this conduit (Figure 4-11).

### Figure 4-11.  Flexible metallic, liquid-tight conduit connector

Connections are made in PVC conduit by cementing two pieces of PVC together (Figure

4-12).  Joints must first be coated with primer.  The cement used is actually a solvent that softens the plastic at the joint and allows the softened areas to flow together to form a weld. The resulting joint is watertight and strong.  PVC conduit can be cut readily with any fine-tooth saw.

### Figure 4-12.  PVC coupling

When you run conduit from one point to another, you often need to make more turns (total of 360() than the NEC allows in a single run.  When this is the case, you can use a fitting called a conduit body.  A conduit body, as defined in the NEC, is "a separate portion of a conduit or tubing system that provides access through a removable cover to the interior of the system at a junction of two or more sections of the system or at a terminal point of the system."  Figure 3-3, page 3-3, shows some of the more common conduit bodies and covers.

A conduit body is put in conduit between two outlets to keep the bends within NEC limits for a single run (Figure 4-13).  As you can see, the run on the left has bends that total 360º, which is all the NEC permits.  Therefore, a conduit body had to be installed so that the conduit could be continued to the box on the right.

Figure 4-13.  Conduit body usage

Conduit must be supported by straps or hangers throughout the entire run (Figure 4-14).

Figure 4-14.  Conduit supports

On a wooden surface, nails or wood screws can be used to secure the straps.  On brick or concrete surfaces, you must first make a hole with a star or carbide drill and then install an expansion anchor.  Use an expansion tool to force the anchors apart, forming a wedge to hold the anchor in the hole.  Secure the strap to the surface with machine screws attached to the anchor.  On tile or other hollow material, secure the straps with toggle bolts.  If the installation is made on metal surfaces, you can drill holes to secure the straps or hangers with machine or sheet-metal screws.

The number of supports needed depends on the type of conduit being used.  Holes or notches in framing members may serve as supports.  EMT requires supports within 3 feet of each outlet box, junction box, cabinet, or fitting and every 10 feet thereafter.  Rigid-steel conduit must also be supported within 3 feet of a box.  The distance between supports may be increased to 20 feet on direct vertical runs of rigid-steel conduit from machine tools and other equipment if threaded couplings are used and the riser is supported at each end.  PVC must be supported as in Table 4-1.

### Table 4-1.  Supporting distances for PVC

| Conduit Size | Maximum Space Between Supports |
| --- | --- |
| 1/2 to 1 inch | 3 feet |
| 1 1/4 to 2 inches | 5 feet |
| 2 1/2 to 3 inches | 6 feet |
| 3 1/2 to 5 inches | 7 feet |
| 7 inches | 8 feet |

In addition, PVC must be supported within 3 feet of each opening.

Flexible metallic conduit must be supported at intervals not to exceed 4 1/2 feet and within 12 inches on each side of every outlet box or fitting.  Exceptions to this are runs of 3 feet or less where flexibility is needed or 6 feet when connecting light fixtures.

After all conduit has been installed, supported, and connected to the boxes, you are ready to install the conductors.

PART B:  INSTALLING CONDUCTORS

Nearly all types of wire may be used in conduit installation; however, the most common type used is moisture-resistant thermoplastic (TW).  To determine the length of wire to be installed, add the length of conduit and the length of wire to be left in the boxes for connections (usually 6 inches for each outgoing wire).  If the conductors are to be connected into the breaker panel add conductor lengths, in feet, equal to the length and width of the breaker panel.

The general procedure for installing conductors in conduit is the same for all types of conduit.  Conductors are installed by pulling them through the conduit.  The pulling is done with a special tool called a fish tape (Figure 4-15).

### Figure 4-15.  Fish tape

The fish tape is fed through the conduit from its storage reel.  The tape is fed in at a

box installed for a switch or receptacle.  The tape is pulled out of the next opening in the line away from the panel box (Figure 4-16).

Figure 4-16.  Use of the fish tape

Conductors are fastened to the end of the tape.  The tape is then pulled or reeled in to draw the conductors through the conduit.  If the run is long, two people are needed for this job.  One feeds the conductors in at one end as the other reels in the fish tape.

In most cases, there will be more than one conductor being fed into the conduit.  It is important to keep the conductors smooth and free of kinks.  Set up the conductor spools so that they unwind freely and can be kept free of bends and crossovers.

When more than one conductor is to be pulled, the connection to the fish tape should be staggered to avoid a bulky connection that would make pulling difficult (Figure 4-18.)

Figure 4-18.  Connecting conductors to the fish tape

If the conductors become twisted, they are difficult to pull around bends.  For particularly long runs or where there are many bends, wires can be coated with a lubricating compound. Noncorrosive lubricating components are available in dry powder form and in paste.

Sometimes, nonmetallic cable, rather than individual conductors, is installed in conduit.  This is done in locations where special protection is needed, such as below grade in residences.  The extra stiffness and larger diameter of cable require that special care be taken when feeding the cable into the conduit to avoid damage to it.

The procedure of pulling conductors between switch or receptacle boxes is continued until the complete system is wired.  Sometimes, if no switch or receptacle box is called for on a long run, a conduit body must be installed near the middle of the run to make conductor installation easier.  Conduit bodies can be used as pull boxes by opening the hatch.  Be sure to leave at least 6 inches of wire at each box to make connections to the switch, receptacle, or fixture that will be installed later.

NOTE:  A pull box is used at the mid-point for long runs of conduit.  Conductors are pulled from the pull box to the start of the run.  Then, conductors are pulled from the mid-point (pull box) to the end of the run.  This eliminates the need to pull heavy conductors over long distances.  Friction between conductors, the conduit, and the weight of the conductors can cause wire (conductor) pulling to be very difficult.

Whenever possible, run conductors from box to box without a break.  In particular, the white- or gray-insulated (neutral) wire should be continued unbroken.  When the fish tape has been reeled in, hold the red or black conductors and pull out enough white wire to reach the next box or the end of the run.  At each box where a connection must be made, leave a loop of white wire.  The wire can be connected by removing a section of insulation without cutting the conductor.  In many cases, the red and black wires can also be continued in this manner.  Continuing conductors in this way reduces the number of connections that must be made in electrical boxes.  This speeds up work and keeps boxes uncrowded.

LESSON 4

PRACTICE EXERCISE

The following items will test your grasp of the material covered in this part of the lesson.  There is only one correct answer for each item.  When you complete the exercise, check your answers with the answer key that follows.  If you answer any item incorrectly, study again that part of the lesson which contains the portion involved.

1.  All but one type of metallic conduit can serve as a grounding conductor.  Which one cannot?

A.  Rigid steel

B.  Flexible

C.  EMT

D.  PVC

2.  Refer to the answer in question 1 and tell why this type of conduit cannot be used as a grounding conductor.

________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

LESSON 4

PRACTICE EXERCISE

ANSWER KEY AND FEEDBACK

Item			Correct Answer and Feedback

1.			B.  	For this reason, flexible conduit should not be used as a grounding conductor.

(page 4-6, para 1).

- The spiral construction of flexible metallic conduit causes it to have a higher electrical resistance per foot than solid metallic conduit.

(page 4-5, para 4).

APPENDIX A

Metric Conversion Chart

This appendix complies with current army directives which state that the metric system will be incorporated into all new publications. Table C-1 is a conversion chart.

Table C-1. Metric conversion chart

| US Units | Multiplied By | Equals Metric Units |
| --- | --- | --- |
| Length |
| Feet | 0.30480 | Meters |
| Inches | 2.54000 | Centimeters |
| Inches | 0.02540 | Meters |
| Inches | 25.40010 | Millimeters |

APPENDIX B

LIST OF COMMON ACRONYMS

ACCP		Army Correspondence Course Program

AIPD		Army Institute for Professional Development

AMEDD	Army Medical Department

AV		autovon

DINFOS	Defense Information School

DSN		Defense Switched Network

EMT		electrical metallic tubing

EN		engineer

FC		flat cable assembly

FM		field manual

JFK		John F. Kennedy

LB		elbow back

LL		elbow left

LR		elbow right

MOS		military occupational specialty

NEC		National Electrical Code

Para		paragraph

PVC		polyvinyl chloride (plastic)

RCOAC	Reserve Component Officer Advanced Course

Reg		regulation

RYE		retirement year ending

SM		soldier's manual

SSN		social security number

STP		soldier training publication

TG		trainer's guide

TM		technical manual

TRADOC	United States Army Training and Doctrine Command

TW		moisture-resistant thermoplastic

US		United States

VA		Virginia

APPENDIX C

RECOMMENDED READING LIST

STP 5-51R12-SM-TG.  Soldier's Manual and Trainer's Guide, MOS 51R, Interior Electrician, Skill Levels 1/2.  27 October 1988.

NOTE:  This publication provides additional information about the material in this subcourse.  You do not need this material to complete this subcourse.

# Text boxes

Pipe

vise

Pipe

reamer

Hacksaw

Conduit

Handle

Cutting wheel

Pipe cutter

14 teeth per inch for large sections of mild material

18 teeth per inch for tough steel

Keep at least two teeth cutting to

avoid breaking the blade

32 teeth per inch for thin tubing

24 teeth per inch for angle iron, heavy pipe, brass, and copper

Cutter wheel

Reamer

Rat-tail file

Reamer

Pipe vise

Pliers

Handle

Dies

Ratchet lock               Die holder

Die against conduit

Rigid-steel conduit     Coupling    Gap between ends     Rigid-steel conduit

Continue 45(

More for 90(

Conduit bend

Handle

Bend

45(

Hickey

EMT bender

Pump handle

Hydraulic pump

Tie bars

Tiepins

Bending dies

Shoe

Pipe

Hydraulic bender

90º(

90º

Box

Box

90º

90(

90(

90(

90(

90º

Total = 360(

LR

LB

T

LL

Stub

A

Stub

Take-up

B

Footrest

Handle

Bender arrow

Take-up mark

18 inches

6 inches

Lip or hook

18 inch mark

Lip or hook

18 inch stub

Bender arrow

Footrest

Take-up mark

Bender star

Step 3

Step 4

Step 2

B

Reference point

Step 1

A

Place arrow opposite your marks

30º

6º

30º(

3 inches

3 inches

30(

30(

Finish line

Bender star

Outside to outside

20 inches

Section to be bent is heated in an electric hotbox

Softened section is bent on preset form,

then cooled with a damp cloth.

Body

Compression

ring

Gland nut

Tubing

Body

Gland Nut

Compression ring

Box connector

Coupling

Coupling

Indentations

Conduit

Bushing

Locknuts

1/2 inch conduit

3/8 inch

Box wall

Clamping

screw

Locknut

Insert conduit

Body of machine steel or malleable iron

O-ring assembly

Gland ring

Locknut hardened steel

Compression nut

Conductor protection

O-ring

shield

Steel grounding ferrule

Liquid-tight conduit

Solvent applied to conduit

Conduit

Coupling

Outlet box

Conduit body

90( bends

45( bends

Outlet box

Coupling

90( bends

90( bends

Outlet box

Outlet box

Fish tape

Conductors are attached to the hook

3rd conductor

2nd conductor

1st conductor