Frame 7EA Borescope Work Scope:

The scope of work includes the management, planning, direct supervision and provision of craft labor as required to complete the inspections.  ProEnergy will complete the borescopes in accordance with OEM recommended practices and recommendations.  Ideally, previously recorded borescope inspection data will be made available so that comparative analysis can be accomplished during the inspection process.  The results of a borescope inspection can be inconclusive or subjective. A borescope inspection is performed to determine the general condition of the equipment and to gather as much information as possible to evaluate the integrity of the equipment and to allow for better operations and maintenance planning.

For optimal borescope inspection of the compressor, the turbine should receive a water wash previous to the inspection. During the inspection, with the oil system in service, the machine will be rotated to allow inspection of the compressor blades and turbine buckets in each “exposed” stage.  The load coupling will be marked to allow reference while turning the machine.  Both rotating and exposed stationary components will be inspected.

Outer and inner borescope plugs will be removed to allow borescope of the compressor section.  The following stages with corresponding plug locations will be inspected:

4th Stage Compressor	30.40″ Aft from Forward Flange Face of the Forward Compressor Case

12th Stage Compressor	5.105″ Aft from Forward Flange Face of the Compressor Discharge Case

17th Stage Compressor	29.635″Aft from Forward Flange Face of the Compressor Discharge Casing

The compressor components will be inspected for foreign object damage, dirt buildup, corrosion, tip erosion, trailing edge thinning, stator root erosion and tip clearance wear.  Only the primary borescope inspection plugs of the compressor case will be utilized during the inspection.

Inspection of the combustion section will be accomplished by removal of the spark plugs and flame detectors.  The primary zones and fuel nozzles will be inspected as accessible through the spark plug and flame detector openings.  The combustion section will be inspected for carbon buildup, hot spots, cracking, bulging, wear, and missing metal or thermal barrier coating.

Outer and inner borescope plugs will be removed to allow borescope of the turbine section.  The following stages with corresponding plug locations will be inspected:

1st Stage Nozzle TE and 1st Stage Bucket LE	8.88″ Aft from Forward Flange Face of the Turbine Casing

1st Stage Bucket TE and 2nd Stage Nozzle LE	12.30″ Aft from Forward Flange Face of the Turbine Casing

2nd Stage Bucket LE and 2nd Stage Nozzle TE	22.97″ Aft from Forward Flange Face of the Turbine Casing

2nd Stage Bucket TE and 3rd Stage Nozzle LE	26.48″ Aft from Forward Flange Face of the Turbine Casing

3rd Stage Bucket LE and 3rd Stage Nozzle TE	37.19″ Aft from Forward Flange Face of the Turbine Casing

Both rotating and exposed stationary components of the turbine will occur during this inspection.  The turbine components will be inspected for foreign object damage, corrosion, tip erosion, trailing edge thinning, stator root erosion and tip clearance wear.  Only the primary borescope inspection plugs the turbine case will be utilized during the inspection.