## Hydraulic
Hydraulic Interconnects
Demin Forwarding Unit 1 - Pumps 0403-A, P0403-S
Tag | Size | Rating | Material | From | To | Pressure | Flowrate | Temp
DWF-1 | 3" | 150# | Stainless sch40 | Tank T-0403 | Demin Forwarding Skid - Unit 1 | 0.5-35psig | 0-115gpm | ambient
DWF-2 | 3" | 150# | Stainless sch40 | Demin Forwarding Skid - Unit 1 | Water Injection Skid - Unit 1 - (X-0405A) | 0-60psig | 0-115gpm | ambient
DWF-3 | 2" | 150# | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 1 | Tank T-0403 | 55-150psig | 0-150gpm | ambient
DWF-4 | 2" | NPT | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 1 | Drain | 0psig |  | ambient
DWF-5 | 2" | NPT | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 1 | Drain | 0psig |  | ambient
Demin Forwarding Unit 2 - Pumps P-0404A, P0404S
Tag | Size | Rating | Material | From | To | Pressure | Flowrate | Temp
DWF-1 | 3" | 150# | Stainless sch40 | Tank T-0403 | Demin Forwarding Skid - Unit 2 | 0.5-35psig | 0-115gpm | ambient
DWF-2 | 3" | 150# | Stainless sch40 | Demin Forwarding Skid - Unit 2 | Water Injection Skid - Unit 2 - (X-0405A) | 0-60psig | 0-115gpm | ambient
DWF-3 | 2" | 150# | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 2 | Tank T-0403 | 55-150psig | 0-150gpm | ambient
DWF-4 | 2" | NPT | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 2 | Drain | 0psig |  | ambient
DWF-5 | 2" | NPT | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 2 | Drain | 0psig |  | ambient
Water Injection Skid - X-0405A
Tag | Size | Rating | Material | From | To | Pressure | Flowrate | Temp
WJ1 | 3" | 150# | Stainless sch40 | Demin Forwarding Skid - Unit 1 | Water Injection Skid - Unit 1 - (X-0405A) | 0-65psig | 0-115gpm | ambient
WJ2 | 3" | 600# | Stainless sch40 | Water Injection Skid | Turbogenerator 1 - X-1201 | 0-500psig | 0-115gpm | ambient
IA1 | 1/2" | NPT | Stainless sch40 | Turbine Control | Water Injection Skid - Unit 1 - (X-0405A) | 90 psig |  | ambient
WIJ1A | 2" | NPT | Carbon Sch40 | Floor Drain | Drain
WIJ1B | 2" | NPT | Carbon Sch40 | Floor Drain | Drain
WIS2 | 1" | NPT | Stainless sch40 | Piping Drain | Drain
Water Injection Skid - X-0405B
Tag | Size | Rating | Material | From | To | Pressure | Flowrate | Temp
WJ1 | 3" | 150# | Stainless sch40 | Demin Forwarding Skid - Unit 2 | Water Injection Skid - Unit 2 - (X-0405B) | 0-65psig | 0-115gpm | ambient
WJ2 | 3" | 600# | Stainless sch40 | Water Injection Skid | Turbogenerator 1 - X-1202 | 0-500psig | 0-115gpm | ambient
IA1 | 1/2" | NPT | Stainless sch40 | Turbine Control | Water Injection Skid - Unit 1 - (X-0405B) | 90 psig |  | ambient
WIJ1A | 2" | NPT | Carbon Sch40 | Floor Drain | Drain
WIJ1B | 2" | NPT | Carbon Sch40 | Floor Drain | Drain
WIS2 | 1" | NPT | Stainless sch40 | Piping Drain | Drain
Liquid Fuel Forwarding Skid - Unit 1
LFF-1 | 4" | 150# | Carbon sch40 | Tank T-1002 | Liquid Fuel Forwarding Skid Inlet - Unit 1 | 0.5-35psi | 0-150gpm | ambient
LFF-2 | 3" | 150# | Carbon sch40 | Liquid Fuel Forwarding Skid - Unit 1 | Turbogenerator 1 - X-1201 | 55-150psig | 0-150gpm | ambient
LFF-3 | 2" | 150# | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 1 | Tank T-1002 | 55-150psig | 0-150gpm | ambient
LFF-4 | 2" | NPT | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 1 | Drain | 0psig |  | ambient
LFF-5 | 2" | NPT | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 1 | Drain | 0psig |  | ambient
LFF-6 | 1" | 150# | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 1 | Diesel Tank T-1002? | 55-150psig | 0-150gpm | ambient
LFF-7 | 1" | 150# | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 1 | Emergency Generator | 55-150psig | 0-150gpm | ambient
Liquid Fuel Forwarding Skid - Unit 2
LFF-1 | 4" | 150# | Carbon sch40 | Tank T-1002 | Liquid Fuel Forwarding Skid Inlet - Unit 12 | 0.5-35psi | 0-150gpm | ambient
LFF-2 | 3" | 150# | Carbon sch40 | Liquid Fuel Forwarding Skid - Unit 2 | Turbogenerator 2 - X-1202 | 55-150psig | 0-150gpm | ambient
LFF-3 | 2" | 150# | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 2 | Tank T-1003 | 55-150psig | 0-150gpm | ambient
LFF-4 | 2" | NPT | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 2 | Drain | 0psig |  | ambient
LFF-5 | 2" | NPT | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 2 | Drain | 0psig |  | ambient
LFF-6 | 1" | 150# | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 2 | Diesel Tank T-1003? | 55-150psig | 0-150gpm | ambient
LFF-7 | 1" | 150# | Carbon Sch40 | Liquid Fuel Forwarding Skid - Unit 2 | Emergency Generator | 55-150psig | 0-150gpm | ambient

## Electric
Electric Interconnects
Demin Forwarding Unit 1 - Pumps 0403-A, P0403-S
Tag | Size | Spec | From | To | Voltage | Breaker
Demin Forwarding Unit 2 - Pumps P-0404A, P0404S
Tag | Size | Spec | From | To | Voltage | Breaker
Water Injection Skid - X-0405A
Tag | Spec |  | From | To | Voltage | Breaker
C566A | 19CX14AWG |  | Turbine Control Panel | JB72 Water Injection Skid
C568 | 6PX16AWG+SH |  | Turbine Control Panel | JB 79 Water Inkection Skid
Water Injection Skid - X-0405B
Tag | Spec |  | From | To | Voltage | Breaker
C566B | 19CX14AWG |  | Turbine Control Panel | JB72 Water Injection Skid
C569 | 6PX16AWG+SH |  | Turbine Control Panel | JB 79 Water Inkection Skid
Liquid Fuel Forwarding Skid Unit 1 - P-1004A, P-1004S
Tag | Size | Spec | From | To | Voltage | Breaker
Liquid Fuel Forwarding Skid Unit 1 - P-1005A, P-1005S
Tag | Size | Spec | From | To | Voltage | Breaker
LOCATION DESCRIPTIONS
173 – JB72 WATER INJECTION SKID LEVEL 3
174 – JB79 WATER INJECTION SKID LEVEL 1
175 – WATER INJECTION SKID 480 VOLT SUPPLY
236 – TURBINE ROOF LOW LEVEL
427 – LIQUID FUEL FORWARDING SKID JB01
429 – 88AB-1 MCC CUBICLE
430 – DEMIN WATER FORWARDING JB01
940 – DEMIN WATER FORWARDING JB02
941 – LIQUID FUEL FORWARDING JB02
942 – CUSTOMER SUPPLIED MCC
CUSTOMER SUPPLIED CABLES (continued)
cable number | to | from | level I #cond | diameter I bend rad | gauge | makeup | purpose | special notes
C875 | 115 | 101 | LEVEL(3) \ |  | 12AWG | 1 CABLE | CONTROL SIGNALS
19 COND
C876 | 114 | 101 | LEVEL (1) \ |  | 18 AWG | 1 CABLE-9 TW SHLD | CONTROL SIGNALS
|  |  | 18 COND |  |  | PAIRS
C877 | 174 | 101 | LEVEL (1) \ |  | 18 AWG | 1 CABLE-9 TW SHLD | CONTROL SIGNALS
|  |  | 18 COND |  |  | PAIRS
C878 | 236 | 101 | LEVEL (1) \ |  | 18 AWG | 1 CABLE-9 TW SHLD | CONTROL SIGNALS
|  |  | 18 COND |  |  | PAIRS
C879 | 173 | 101 | LEVEL(3) \ |  | 12AWG | 1 CABLE | CONTROL SIGNALS
19 COND
C880 | 942 | 101 | LEVEL(3) \ |  | 12AWG | 1 CABLE | CONTROL SIGNALS
19 COND
C881 | 429 | 101 | LEVEL(3) \ |  | 12AWG | 1 CABLE | CONTROL SIGNALS
8 COND
C882 | 231 | 101 | LEVEL(3) \ |  | 12AWG | 1 CABLE | CONTROL SIGNALS
19 COND
C883 | 942 | 101 | LEVEL(3) \ |  | 12AWG | 1 CABLE | CONTROL SIGNALS
19 COND
C884 | 392 | 429 | LEVEL(4) \ 3COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88AB-1
C885 | 175 | 183 | LEVEL(4) \ 3COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 88WN-1
C886 | 115 | 429 | LEVEL(4) \ 3COND |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY 23AB-1
C887 | 941 | 942 | LEVEL(4)\ |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY P203A
3COND
C888 | 941 | 942 | LEVEL(4)\ |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY P203B
3COND
C889 | 940 | 942 | LEVEL(4)\ |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY P400A
3COND
C890 | 940 | 942 | LEVEL(4)\ |  |  | SIZED BY CUSTOMER | 3 PH. SUPPLY P400B
3COND
C891 | 430 | 101 | LEVEL(3) \ |  | 12 AWG | 1 CABLE | CONTROL SIGNALS
6 COND
C892 | 430 | 101 | LEVEL (1) \ |  | 18 AWG | 1 CABLE-9 TW SHLD | CONTROL SIGNALS
|  |  | 6 COND |  |  | PAIRS
C893 | 427 | 101 | LEVEL(3) \ |  | 12 AWG | 1 CABLE | CONTROL SIGNALS
6 COND
C894 | 427 | 101 | LEVEL (1) \ |  | 18 AWG | 1 CABLE-9 TW SHLD | CONTROL SIGNALS
|  |  | 6 COND |  |  | PAIRS
101 TURBINE CONTROL PANEL
C875 | 115 JB002 ACCESSORY BASE LEVEL 3 | 3 | 19 | 12 AWG
C876 | 114 JB001 ACCESSORY BASE LOW LEVEL | 1 | 18 | 18 AWG
C877 | 174 JB79 WATER INJECTION SKID LEVEL 1 | 1 | 18 | 18 AWG
C878 | 236 TURBINE ROOF LOW LEVEL | 1 | 12 | 18 AWG
C879 | 173 JB72 WATER INJECTION SKID LEVEL 3 | 3 | 19 | 12 AWG
C880 | 942 CUSTOMER SUPPLIED MCC | 3 | 19 | 12 AWG
C881 | 429 88AB-1 MCC CUBICLE | 3 | 8 | 12 AWG
C882 | 231 JB019B TURBINE OFF BASE LEVEL-3 | 3 | 19 | 12 AWG
C883 | 942 CUSTOMER SUPPLIED MCC | 3 | 19 | 12 AWG
C891 | 430 DEMIN WATER FORWARDING JB01 | 3 | 6 | 12 AWG
C892 | 430 DEMIN WATER FORWARDING JB01 | 1 | 6 | 18 AWG
C893 | 427 LIQUID FUEL FORWARDING JB01 | 3 | 6 | 12 AWG
C894 | 427 LIQUID FUEL FORWARDING JB01 | 1 | 6 | 18 AWG
115 JB002 ACCESSORY BASE LEVEL 3
cable | to | lev | #cnd | Gauge
C875 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG
C886 | 429 88AB-1 MCC CUBICLE | 3 | 3 | CUST
173 JB72 WATER INJECTION SKID LEVEL 3
cable | To | lev | #cnd | Gauge
C879 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG
174 JB79 WATER INJECTION SKID LEVEL 1
cable | To | lev | #cnd | Gauge
C877 | 101 TURBINE CONTROL PANEL | 1 | 18 | 18 AWG
175 WATER INJECTION SKID 480 VOLT SUPPLY
cable | To | lev | #cnd | Gauge
C885 | 183 AUXILIARY POWER TRANSFORMER | 1 | 3 | CUST
183 AUXILARY POWER TRANSFORMER
C885 | 175 WATER INJECTION SKID 480 VOLT SUPPLY | 4 | 3 | CUST
231 JB019B TURBINE OFF CASE RACK LEVEL 3
C882 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG
236 TURBINE ROOF LOW LEVEL
cable | To | lev | #cnd | Gauge
C878 | 101 TURBINE CONTROL PANEL | 1 | 12 | 18 AWG
392 JB004 ACCESSORY BASE LEVEL 4
cable | To | lev | #cnd | Gauge
C884 | 429 88AB-1 MCC CUBICLE | 4 | 3 | CUST
427 LIQUID FUEL FORWARDING SKID JB01
cable | To | lev | #cnd | Gauge
C893 | 101 TURBINE CONTROL PANEL | 3 | 6 | 12 AWG
C894 | 101 TURBINE CONTROL PANEL | 1 | 6 | 18 AWG
429 88AB-1 MCC CUBICLE
cable | To | lev | #cnd | Gauge
C884 | 392 JB004 ACCESSORY BASE LEVEL 4 | 4 | 3 | CUST
C886 | 115 JB002 ACCESSORY BAST LEVEL 3 | 3 | 3 | CUST
C881 | 101 TURBINE CONTROL PANEL | 3 | 8 | 12 AWG
430 DEMIN WATER FORWARDING JB01
cable | To | lev | #cnd | Gauge
C891 | 101 TURBINE CONTROL PANEL | 3 | 6 | 12 AWG
C892 | 101 TURBINE CONTROL PANEL | 1 | 6 | 18 AWG
940 DEMIN WATER FORWARDING JB02
cable | To | lev | #cnd | Gauge
C889 | 942 CUSTOMER SUPPLIED MCC | 4 | 3 | CUST
C890 | 942 CUSTOMER SUPPLIED MCC | 4 | 3 | CUST
941 LIQUID FUEL FORWARDING JB02
cable | To | lev | #cnd | Gauge
C887 | 942 CUSTOMER SUPPLIED MCC | 4 | 3 | CUST
C888 | 942 CUSTOMER SUPPLIED MCC | 4 | 3 | CUST
942 CUSTOMER SUPPLIED MCC
cable | To | lev | #cnd | Gauge
C880 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG
C883 | 101 TURBINE CONTROL PANEL | 3 | 19 | 12 AWG
C887 | 941 DEMIN WATER FORWARDING JB02 | 4 | 3 | CUST
C888 | 941 DEMIN WATER FORWARDING JB02 | 4 | 3 | CUST
C889 | 940 LIQUID FUEL FORWARDING JB02 | 4 | 3 | CUST
C890 | 940 LIQUID FUEL FORWARDING JB02 | 4 | 3 | CUST