## CABLE SUMMARY
CABLE SUMMARY CHANGES
ADDITIONS TO SECTION: LOCATION DESCRIPTIONS
173 - JB072 WATER INJECTION SKID LEVEL 3
174 - JB079 WATER INJECTION SKID LOW LEVEL
236 - TURBINE ROOF PANEL LOW LEVEL
ADDITIONS TO SECTION: CUSTOMER SUPPLIED CABLES
cable | to | from | level / | diameter / | gauge | makeup | purpose | special
number |  |  | # cond | bend rad |  |  |  | notes
W026 | 101 | 114 | LEVEL(3)/ |  | 18 AWG | 1CABLE-9 TW SHLD | LIQUID FUEL DEVICES
|  |  | 18 COND |  |  | PAIRS
W032 | 101 | 115 | LEVEL(3)/ |  | 12 AWG | 1 CABLE | LIQUID FUEL DEVICES
19 COND
W211 | 101 | 231 | LEVEL(3)/ |  | 12 AWG | 1 CABLE | LIQUID FUEL DEVICES
12 COND
W212 | 101 | 231 | LEVEL(3)/ |  | 12 AWG | 1 CABLE | LIQUID FUEL DEVICES
12 COND
C029 | 392 | 334 | LEVEL(4)/ |  | 4 AWG | 1 CABLE | 3 PH. SUPPLY
|  |  | 3 COND |  |  |  | 88AB-1
C566A | 101 | 173 | LEVEL(3)/ |  | 12 AWG | 1 CABLE | LIQUID FUEL DEVICES
7 COND
C566B | 101 | 173 | LEVEL(3)/ |  | 12 AWG | 1 CABLE | LIQUID FUEL DEVICES
7 COND
C568 | 101 | 174 | LEVEL(1)/ |  | 18 AWG | 1CABLE-6 TW SHLD | LIQUID FUEL DEVICES
|  |  | 12 COND |  |  | PAIRS
C569 | 101 | 174 | LEVEL(1)/ |  | 18 AWG | 1CABLE-6 TW SHLD | LIQUID FUEL DEVICES
|  |  | 12 COND |  |  | PAIRS
C570 | 101 | 236 | LEVEL(1)/ |  | 18 AWG | 1CABLE-6 TW SHLD | LIQUID FUEL DEVICES
|  |  | 12 COND |  |  | PAIRS
CHANGES TO INDIVIDUAL LOCATION LISTS:
101 TURBINE CONTROL PANEL
cable | to |  |  |  |  | level | # cond | gauge
W026 | 114 JB001 ACCESSORY BASE LOW LEVEL |  |  |  |  | 3 | 18 | 18 AWG
W032 | 115 JB002 ACCESSORY BASE LEVEL 3 |  |  |  |  | 3 | 19 | 12 AWG
W211 | 231 JB019B TURBINE OFF BASE RACK LEVEL 3 |  |  |  |  | 3 | 12 | 12 AWG
W212 | 231 JB019B TURBINE OFF BASE RACK LEVEL 3 |  |  |  |  | 3 | 12 | 12 AWG
C566A | 173 JB72 WATER INJECTION SKID LEVEL 3 |  |  |  |  | 3 | 7 | 12 AWG
C566B | 173 JB72 WATER INJECTION SKID LEVEL 3 |  |  |  |  | 3 | 7 | 12 AWG
C568 | 174 JB79 WATER INJECTION SKID LOW LEVEL |  |  |  |  | 1 | 12 | 18 AWG
C569 | 174 JB79 WATER INJECTION SKID LOW LEVEL |  |  |  |  | 1 | 12 | 18 AWG
C570 | 236 TURBINE ROOF PANEL LOW LEVEL |  |  |  |  | 1 | 12 | 18 AWG
114 JB001 ACCESORY BASE LOW LEVEL
cable | to |  |  |  |  | level | # cond | gauge
W026 | 101 TURBINE CONTROL PANEL |  |  |  |  | 3 | 18 | 18 AWG
115 JB002 ACCESORY BASE LEVEL 3
cable | to |  |  |  |  | level | # cond | gauge
W032 | 101 TURBINE CONTROL PANEL |  |  |  |  | 3 | 19 | 12 AWG
173 JB72 WATER INJECTION SKID LEVEL 3
cable | to |  |  |  |  | level | # cond | gauge
C566A | 101 TURBINE CONTROL PANEL |  |  |  |  | 3 | 7 | 12 AWG
C566B | 101 TURBINE CONTROL PANEL |  |  |  |  | 3 | 7 | 12 AWG
174 JB79 WATER INJECTION SKID LOW LEVEL
cable | to |  |  |  |  | level | # cond | gauge
C568 | 101 TURBINE CONTROL PANEL |  |  |  |  | 1 | 12 | 18 AWG
C569 | 101 TURBINE CONTROL PANEL |  |  |  |  | 1 | 12 | 18 AWG
231 JB019B TURBINE OFF BASE LEVEL 3
cable | to |  |  |  |  | level | # cond | gauge
W211 | 101 TURBINE CONTROL PANEL |  |  |  |  | 3 | 12 | 12 AWG
W212 | 101 TURBINE CONTROL PANEL |  |  |  |  | 3 | 12 | 12 AWG
236 TURBINE ROOF PANEL LOW LEVEL
cable | to |  |  |  |  | level | # cond | gauge
C570 | 101 TURBINE CONTROL PANEL |  |  |  |  | 1 | 12 | 18 AWG
334 | PEECC MOTOR CONTROL CENTER
cable | to |  |  |  |  | level | # cond | gauge
C029 | 392 JB004 ACCESSORY BASE LEVEL 4 |  |  |  |  | 4 | 3 | 4 AWG
392 | JB004 ACCESSORY BASE LEVEL 4
cable | to |  |  |  |  | level | # cond | gauge
C029 | 334 PEECC MOTOR CONTROL CENTER |  |  |  |  | 4 | 3 | 4 AWG

## WIRING INTERCONNECT
WIRING INTERCONNECTION CHANGES
CABLE: C014 |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**USED SPARE CONDUCTORS** |  |  |  |  | 363 | JB130 GAS FUEL MODULE
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 363
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  | 3 2 | 1 2 RED | 126 | 33PG-1-3 | NO |  | TBA | 03
|  |  | 3 3 | 1 3 RED | 128 | 33PG-2-4 | NO |  | TBA | 06
|  |  | 3 4 | 1 4 RED | 7610 | 63PG-1 | NO |  | TBA | 21
|  |  | 3 5 | 1 5 RED | 257 | 20PG-1 | 0 1 |  | TBA | 27
|  |  | 3 6 | 1 6 RED | 276 | 20PG-2 | 0 1 |  | TBA | 28
|  |  | 3 7 | 17 RED | 7216 | 20VG-2 | 0 1 |  | TBA | 35
NOTES FOR CABLE C014
NUMBER | NOTES
1 | CONDUCTOR 19 (107) IS THE COMMOM FOR THE SIGNALS ON CONDUCTORS 05-11, 23 AND 28.
2 | CONDUCTOR 18 (108) IS THE COMMON FOR THE SIGNALS ON CONDUCTORS 13 AND 20-22.
3 | ADD THE FOLLOWING JUMPERS IN (363) JB130 GAS FUEL MODUULE: TBA-(0111) TO TBA-(008) TBA-(008) TO TBB-(001)
4 | REMOVE THE FOLLOWING JUMPERS IN (363) JB130 GAS FUEL MODULE: TBA-(007) TO TBA-(008) TBA-(010) TO TBA-(011)
CABLE: C029 |  |  | CONNECTS: |  | 334 | PEECC MOTOR CONTROL CENTER
**NEW CABLE** |  |  |  |  | 392 | JB004 ACCESSORY BASE LEVEL-4
FROM LOCATION 334 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 392
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  | 0 1 | 0 1 BLK | T1-AB-1 | 88AB-1 | T1 |  | TBVV | 001
|  |  | 0 2 | 0 2 BLK | T2-AB-1 | 88AB-1 | T2 |  | TBVV | 002
|  |  | 0 3 | 0 3 BLK | T3-AB-1 | 88AB-1 | T3 |  | TBVV | 003
NOTES FOR CABLE C029
NUMBER | NOTES
1 | NEW CABLE
CABLE: C037 |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**USED SPARE CONDUCTORS** |  |  |  |  | 115 | JB002 ACCESSORY BASE LEVEL-3
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 115
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  | 1 7 | 1 7 BLK | 650 | 63AD-1A | NO |  | TBD | 0 2 0
|  |  | 1 8 | 1 8 BLK | 2652 | 63AD-1B | NO |  | TBD | 0 1 9
|  |  | 1 9 | 1 9 BLK | 5601 | 63AD-1C | NO |  | TBD | 0 1 8
|  |  | 2 0 | 2 0 BLK | 130 | 63HL-1 | NO |  | TBH | 0 0 2
|  |  | 2 1 | 2 1 RED | 621 | 63HL-2 | NO |  | TBH | 0 0 3
|  |  | 2 2 | 2 2 RED | 122 | 63HL-3 | NO |  | TBH | 0 0 4
|  |  | 2 3 | 2 3 RED | 148 | 63FL-2 | NO |  | TBG | 0 0 6
|  |  | 2 4 | 2 4 RED | 633 | 63AF-1 | NO |  | TBH | 0 0 1
|  |  | 3 6 | 3 6 RED | 218 | 20CF-1 | 0 1 |  | TBH | 009
CABLE:C200 |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**USED SPARE CONDUCTORS** |  |  |  |  | 233 | JB020A TURBINE OFF BASE RACK LOW LEVEL
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 233
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  | 0 1 | 01 YEL | SP
|  |  | 0 2 | 01 RED | SP
|  |  | 0 3 | 02 YEL | 8437 | AA-TI-1A | YEL |  | TBB | 007
|  |  | 0 4 | 02 RED | 8438 | AA-TI-1A | RED |  | TBB | 008
|  |  | 0 5 | 3 YEL
|  |  | 0 6 | 3 RED
|  |  | 0 7 | 4 YEL | 8439 | AA-TI-1B | YEL |  | TBF | 005
|  |  | 0 8 | 4 RED | 8440 | AA-TI-1B | RED |  | TBF | 006
NOTES FOR CABLE C200
NUMBER | NOTES
1 | "B" ELEMENTS NOT CONNECTED IN (101) TURBINE CONTROL PANEL. THESE ARE SPARE ELEMENTS.
2 | SHOW SHLDS GROUNDED TO SHLD COM. IN MARE VI.
CABLE: C566A |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**NEW CABLE** |  |  |  |  | 173 | JB72 WATER INJECTION SKID LEVEL 3
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 173
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  | 01 | 01 BLK | 107 | P125VDC | COM |  | TBA | 016
|  |  | 02 | 02 BLK | 2137 | 63WN-1 | NO |  | TBB | 001
|  |  | 03 | 03 BLK | 1694 | 63WN-3 | NC |  | TBB | 003
|  |  | 04 | 04 BLK | 1600 | 26JS-2 | NC |  | TBB | 004
|  |  | 05 | 05 BLK | 9109 | 30WN-1 | NC |  | TBB | 006
|  |  | 06 | 06 BLK | 9110 | 84WN-1 | NO |  | TBB | 008
|  |  | 07 | 07 BLK | SP
NOTES FOR CABLE C566A
NUMBER | NOTES
1 | NEW CABLE
2 | CABLES C566A AND C566B CAN BE COMBINED TO ONE CABLE
CABLE: C566B |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**NEW CABLE** |  |  |  |  | 173 | JB72 WATER INJECTION SKID LEVEL 3
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 173
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  | 01 | 01 BLK | 2685 | 52WN-1 | NO |  | TBB | 010
|  |  | 02 | 02 BLK | 214 | 20WN-1 | 0 1 |  | TBB | 019
|  |  | 03 | 03 BLK | 2124 | 20WN-1 | FU-04 |  | TBB | 020
|  |  | 04 | 04 BLK | 7599 | 4WN-1X | 0 1 |  | TBB | 021
|  |  | 05 | 05 BLK | 7598 | 4WN-1X | FU-05 |  | TBB | 022
|  |  | 06 | 06 BLK | SP
|  |  | 07 | 07 BLK | SP
NOTES FOR CABLE C566B
NUMBER | NOTES
1 | NEW CABLE
2 | CABLES C566A AND C566B CAN BE COMBINED TO ONE CABLE
CABLE: C568 |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**NEW CABLE** |  |  |  |  | 174 | JB79 WATER INJECTION SKID LEVEL 1
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 174
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  |  | 01 SHD | E3900 | 96WF-1 | SHD |  | TBC | 003
|  |  | 01 | 01 ORN | 3900 | 96WF-1 | POS |  | TBC | 002
|  |  | 02 | 01 BLK | 3901 | 96WF-1 | NEG |  | TBC | 001
|  |  |  | 02 SHD | E3902 | 96WF-2 | SHD |  | TBC | 006
|  |  | 03 | 02 ORN | 3902 | 96WF-2 | POS |  | TBC | 005
|  |  | 04 | 02 BLK | 3903 | 96WF-2 | NEG |  | TBC | 004
|  |  |  | 03 SHD | E3904 | 96WF-3 | SHD |  | TBC | 009
|  |  | 05 | 03 ORN | 3904 | 96WF-3 | POS |  | TBC | 008
|  |  | 06 | 03 BLK | 3905 | 96WF-3 | NEG |  | TBC | 007
04 SHD
|  |  | 07 | 04 ORN | SP
|  |  | 08 | 04 BLK | SP
05 SHD
|  |  | 09 | 05 ORN | SP
|  |  | 10 | 05 BLK | SP
06 SHD
|  |  | 11 | 06 ORN | SP
|  |  | 12 | 06 BLK | SP
NOTES FOR CABLE C568
NUMBER | NOTES
1 | NEW CABLE
CABLE: C569 |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**NEW CABLE** |  |  |  |  | 174 | JB79 WATER INJECTION SKID LEVEL 1
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 174
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  |  | 01 SHD | E6978 | 97WN-1 | SHD |  | TBD | 003
|  |  | 01 | 01 ORN | 6978 | 97WN-1 | POS |  | TBD | 002
|  |  | 02 | 01 BLK | 6979 | 97WN-1 | NEG |  | TBD | 001
|  |  |  | 02 SHD | E6974 | 96WN-4 | SHD |  | TBD | 006
|  |  | 03 | 02 ORN | 6974 | 96WN-4 | POS |  | TBD | 005
|  |  | 04 | 02 BLK | 6975 | 96WN-4 | NEG |  | TBD | 004
|  |  |  | 03 SHD | E6976 | 96WP-1 | SHD |  | TBD | 009
|  |  | 05 | 03 ORN | 6976 | 96WP-1 | POS |  | TBD | 008
|  |  | 06 | 03 BLK | 6977 | 96WP-1 | NEG |  | TBD | 007
04 SHD
|  |  | 07 | 04 ORN | SP
|  |  | 08 | 04 BLK | SP
05 SHD
|  |  | 09 | 05 ORN | SP
|  |  | 10 | 05 BLK | SP
06 SHD
|  |  | 11 | 06 ORN | SP
|  |  | 12 | 06 BLK | SP
NOTES FOR CABLE C569
NUMBER | NOTES
1 | NEW CABLE
CABLE: C570 |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**NEW CABLE** |  |  |  |  | 236 | TURBINE ROOF LOW LEVEL
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 236
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  |  | 01 SHD |  | 96PLP-1 | SHD |  | TBA | 012
|  |  | 01 | 01 ORN |  | 96PLP-1 | POS |  | TBA | 010
|  |  | 02 | 01 BLK |  | 96PLP-1 | NEG |  | TBA | 011
|  |  |  | 02 SHD |  | 96PLS-1 | SHD |  | TBA | 006
|  |  | 03 | 02 ORN |  | 96PLS-1 | POS |  | TBA | 004
|  |  | 04 | 02 BLK |  | 96PLS-1 | NEG |  | TBA | 005
|  |  |  | 03 SHD |  | 96PWP-1 | SHD |  | TBA | 009
|  |  | 05 | 03 ORN |  | 96PWP-1 | POS |  | TBA | 007
|  |  | 06 | 03 BLK |  | 96PWP-1 | NEG |  | TBA | 008
04 SHD
|  |  | 07 | 04 ORN | SP
|  |  | 08 | 04 BLK | SP
05 SHD
|  |  | 09 | 05 ORN | SP
|  |  | 10 | 05 BLK | SP
06 SHD
|  |  | 11 | 06 ORN | SP
|  |  | 12 | 06 BLK | SP
NOTES FOR CABLE C570
NUMBER | NOTES
1 | NEW CABLE
CABLE: W026 |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**NEW CABLE** |  |  |  |  | 114 | JB001 ACCESSORY BASE LOW LEVEL
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 114
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  |  | 01 SHD |  |  | SHD
|  |  | 01 | 01 WH | SP
|  |  | 02 | 01 BLK | SP
|  |  |  | 02 SHD |  |  | SHD
|  |  | 03 | 02 WH | SP
|  |  | 04 | 02 BLK | SP
|  |  |  | 03 SHD |  |  | SHD
|  |  | 05 | 03 WH | SP
|  |  | 06 | 03 BLK | SP
|  |  |  | 04 SHD | E308 | 77FD-1 | SHD |  | TBC | 003
|  |  | 07 | 04 WH | 309 | 77FD-1 | SIG+ |  | TBC | 002
|  |  | 08 | 04 BLK | 308 | 77FD-1 | SIG- |  | TBC | 001
|  |  |  | 05 SHD | E310 | 77FD-2 | SHD |  | TBC | 006
|  |  | 09 | 05 WH | 311 | 77FD-2 | SIG+ |  | TBC | 005
|  |  | 10 | 05 BLK | 310 | 77FD-2 | SIG- |  | TBC | 004
|  |  |  | 06 SHD | E1368 | 77FD-3 | SHD |  | TBC | 009
|  |  | 11 | 06 WH | 1369 | 77FD-3 | SIG+ |  | TBC | 008
|  |  | 12 | 06 BLK | 1368 | 77FD-3 | SIG- |  | TBC | 007
|  |  |  | 07 SHD | E362 | 65FP-1 | SHD |  | TBC | 012
|  |  | 13 | 07 WH | 363 | 65FP-1 | YEL |  | TBC | 010
|  |  | 14 | 07 BLK | 362 | 65FP-1 | GRN |  | TBC | 011
|  |  |  | 08 SHD | E364 | 65FP-1 | SHD |  | TBC | 015
|  |  | 15 | 08 WH | 365 | 65FP-1 | RED |  | TBC | 013
|  |  | 16 | 08 BLK | 364 | 65FP-1 | WHT |  | TBC | 014
|  |  |  | 09 SHD | E2388 | 65FP-1 | SHD |  | TBC | 018
|  |  | 17 | 09 WH | 2389 | 65FP-1 | ORN |  | TBC | 016
|  |  | 18 | 09 BLK | 2388 | 65FP-1 | BLU |  | TBC | 017
|  |  | 19 | 10 BLK
NOTES FOR CABLE W026
NUMBER | NOTES
1 | NEW CABLE
CABLE: W032 |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**NEW CABLE** |  |  |  |  | 115 | JB002 ACCESSORY BASE LEVEL-3
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 115
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  | 01 | 01 BLK | 241 | 20AA-1 | 0 1 |  | TBH | 007
|  |  | 02 | 02 BLK | 217 | 20AB-1 | 0 1 |  | TBH | 008
|  |  | 03 | 03 BLK | SP
|  |  | 04 | 04 BLK | SP
|  |  | 05 | 05 BLK | 107 | 63LF-1 | C |  | TBC | 008
|  |  | 06 | 06 BLK | 684 | 63LF-1 | NC |  | TBG | 005
|  |  | 07 | 07 BLK | SP
|  |  | 08 | 08 BLK | SP
|  |  | 09 | 09 BLK | 5620 | 33FK-1 | NO |  | TBG | 009
|  |  | 10 | 10 BLK | 5619 | 33FK-2 | NO |  | TBG | 010
|  |  | 11 | 11 BLK | 166 | 33FL-1 | NO2 |  | TBG | 011
|  |  | 12 | 12 BLK | 169 | 33FL-2 | NO2 |  | TBG | 012
|  |  | 13 | 13 BLK | 107 | P125VDC | COM |  | TBC | 001
|  |  | 14 | 14 BLK | 9295 | 63LF-8 | NC |  | TBG | 013
|  |  | 15 | 15 BLK | 1220 | 63LF-9 | NC |  | TBG | 014
|  |  | 16 | 16 BLK | 5627 | 20FK-1 | 01 |  | TBG | 015
|  |  | 17 | 17 BLK | 108 | 20FK-1 | 02 |  | TBB | 010
|  |  | 18 | 18 BLK | 232 | 20FL-1 | 01 |  | TBG | 016
|  |  | 19 | 19 BLK | 233 | 20FL-1 | 02 |  | TBG | 017
NOTES FOR CABLE W032
NUMBER | NOTES
1 | NEW CABLE
2 | CONDUCTOR 13 (107) IS THE COMMON FOR THE SIGNALS ON CONDUCTORS 05, 06, 09 THRU 12, 14 AND 15.
CABLE: W211 |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**NEW CABLE** |  |  |  |  | 231 | JB019B TURBINE OFF BASE RACK LEVEL-3
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 235
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  | 01 | 01 BLK | 107 | 33WP-1 | C |  | TBD | 007
|  |  | 02 | 02 BLK | 6319 | 33WP-1 | NO |  | TBB | 002
|  |  | 03 | 03 BLK | 219 | 20PL-1 | 0 1 |  | TBC | 011
|  |  | 04 | 04 BLK | SP
|  |  | 05 | 05 BLK | 7749 | 20BP-1 | 0 1 |  | TBC | 010
|  |  | 06 | 06 BLK | 108QD1 | 20BP-1 | 0 2 |  | TBD | 010
|  |  | 07 | 07 BLK | 7247 | 20PW-1 | 0 1 |  | TBB | 009
|  |  | 08 | 08 BLK | 108 | 20PW-1 | 0 2 |  | TBD | 019
|  |  | 09 | 09 BLK | SP
|  |  | 10 | 10 BLK | SP
|  |  | 11 | 11 BLK | SP
|  |  | 12 | 12 BLK | SP
NOTES FOR CABLE W211
NUMBER | NOTES
1 | NEW CABLE
CABLE: W212 |  |  | CONNECTS: |  | 101 | TURBINE CONTROL PANEL
**NEW CABLE** |  |  |  |  | 231 | JB019B TURBINE OFF BASE RACK LEVEL-3
FROM LOCATION 101 |  |  | CABLE |  | DEVICE |  |  | TO LOCATION 235
INT LOC | TERM BD | TERM | PIN | COND | WIRE # | DEVICE | DESC | INT LOC | TERM BD | TERM
|  |  | 01 | 08 BLK | 221 | 20PL-2 | 0 1 |  | TBC | 008
|  |  | 02 | 09 BLK | 108QD2 | 20PL-2 | 0 2 |  | TBD | 012
|  |  | 03 | 10 BLK | 7144 | 20PL-3 | 0 1 |  | TBB | 010
|  |  | 04 | 11 BLK | 108QD2 | 20PL-3 | 0 2 |  | TBD | 017
|  |  | 05 | 12 BLK | 7262 | 20PL-4 | 0 1 |  | TBB | 011
|  |  | 06 | 13 BLK | 108QD2 | 20PL-4 | 0 2 |  | TBD | 017
|  |  | 07 | 14 BLK | 107 | 33PL-1 | C |  | TBD | 001
|  |  | 08 | 15 BLK | 5645 | 33PL-1 | NO |  | TBC | 005
|  |  | 09 | 16 BLK | 107 | 33PL-2 | C |  | TBD | 002
|  |  | 10 | 17 BLK | 5159 | 33PL-2 | NO |  | TBC | 006
|  |  | 11 | 18 BLK | SP
|  |  | 12 | 19 BLK | SP
NOTES FOR CABLE W212
NUMBER | NOTES
1 | NEW CABLE