Design Basis – Dual Fuel Modification of 7EA Gas Turbine

Summary:

ProEnergy has developed a Dual Fuel Modification Package to be installed on GE 7EA Gas Turbines originally built by the OEM as “Gas Only” units. This modification, when applied to a “Gas Only” unit, will allow it to start and operate on natural gas or distillate fuel.  The Dual Fuel Modification Package was developed through evaluations of several existing GE 7EA dual fuel units. ProEnergy developed systems for this package that provide similar functionality and are comprised of equipment that has been proven in the same application.

ProEnergy has developed these systems to fit into the existing turbine and accessory packages so that they will not interfere with existing equipment or future modifications. ProEnergy has performed engineering evaluations for new equipment that have not been proven in this application.

ProEnergy used industry standards and general practices to fabricate and assemble equipment for the dual fuel modification. ProEnergy followed ASME pressure and piping codes for fabrication works.

Derwick / EDC supplied drawings and documentation to ProEnergy specifically for the units being modified. These documents included all drawings, specifications, and documentation for the equipment that was issued by the original OEM and their sub vendors.  These drawings were evaluated and modified to reflect the duel fuel modification that will be applied to the units.

The turbine unit serial numbers that will be modified to dual fuel are 298034 and 298035 manufactured by General Electric.

Narrative – Systems Overview

ProEnergy performed various take offs of existing dual fuel systems to develop the dual fuel modification package.  Below is a system by system overview that will be installed on the turbines noted above.

Liquid Fuel System:

A complete liquid fuel system will be added to the Margarita unit. Several of the controlled components that will be added will be connected into the existing hydraulic and lube oil systems. The system will include several instruments and devices which will provide the input and feedback signals to the control system.  Below are several of the major components that will be utilized.

- Liquid Fuel Duplex Filter and Transfer Valve – Manufactured by Hilco / Hilliard

- Liquid Fuel Stop Valve with limit switch feedback– Young & Franklin

- Main Fuel Pump – Colfax / IMO

- Liquid Fuel By-pass Valve with servo control and LVDT feedback – Young & Franklin

- Fuel Pump Solenoid Clutch  – Carlyle Johnson

- Flow Divider with magnetic speed pick-ups  – Roper Industries

- Isolation Valve with limit switch feedback– Parker Hannifin Corporation

- Solenoid Stop Valve – Ruggles-Klingemann Mfg.

- False Start Drain Valves – RG Laurence

Atomizing Air System:

A complete atomizing air system will be added to the Margarita unit. Several of the components that will be added will be connected into the existing lube oil, control air, and cooling water systems. The system will include several instruments that will be added which will provide the input and feedback signals to the control system.  Below are several of the major components that will be utilized.

- Atomizing Air Heat Exchanger – ITT Standard

- Bypass Control Valves – Contromatics

- Atomizing Air Booster Compressor  & motor– Gardner Denver

- Atomizing Air Check Valves – Meuller “Chexter Check”

- Main Atomizing Air Compressor – Atlas Copco

- Atomizing Air Filter – Hilco Hilliard

- Flexible Hoses – MicroFlex

One of the new items that will be incorporated into the design for Margarita is the motor starter and breaker for the atomizing air booster compressor. The breaker / motor starter will be installed in the PECC and controlled by the turbine control system.  See design details in the technical specifications.

The atomizing air system piping was designed and fabricated according to existing systems. All of the piping is fabricated with stainless steel pipe to eliminate any sources of contamination.

Purge Air system:

The existing purge air system for the gas fuel system will be modified.  A purge air heat exchanger will be added to cool the purge air, a purge panel with solenoid valves to control air flow to the three headers in the turbine compartment; one for the primary fuel nozzles, one for the secondary fuel nozzles, and one for water injection. A purge protection panel will be added to the roof of the turbine compartment to monitor pressures in the three headers. These pressure transmitters will provide feedback to the control system to alert if a problem arises. The purge air system will include several other instruments which will provide the input and feedback signals to the control system. Below are several of the major components that will be utilized.

- Purge Air Heat Exchanger – ITT Standard

- Purge Valves – 3 way – Jensen Aircraft Systems

- Check Valves –  Jensen Aircraft Systems

- Purge Valves (air operated)– Flowtek

The piping and tubing for this system is fabricated with stainless steel to maintain cleanliness of the air to the fuel nozzles. The connections between the purge air headers to the nozzles are made with tubing connections to ease removal and reassembly during maintenance events.

Fuel Management Spool:

The Fuel Management Spool was added as an additional feature to the liquid fuel system. A flow meter is included in the fuel metering spool and has a totalizing feature that ties directly into the turbine control system. A bypass around the flow meter is provided in the case of maintenance requirements on the meter.

The spool also includes a solenoid stop valve for secondary protection for the turbine and a pressure control valve to eliminate any significant fuel pressure fluctuations at the input to the turbine.

- Fuel Flow Meter - Brodie Metering Co.

- Flow Stop Valve  (secondary protection) CR-Tec

- Pressure Control Valve – Fischer

Cooling Water:

The existing cooling water system will be modified to include two additional heat loads. The atomizing air heat exchanger and purge air heat exchanger will create an additional 42,050 BTU/Min heat load to the system for a total of 95,250 BTU/Min.

The existing cooling water module supplied with the unit was evaluated for the additional heat load and for the new design conditions at Margarita Island. This evaluation was performed by GEA, the original designer and provider of the cooling water module.

Using the new design basis below, the results of the cooling water system evaluation are shown in Table 1.

- Maximum Ambient Temperature:  32 Deg C (91.0 deg F)

- Maximum Relative Humidity:  90%

- Altitude:  Sea Level

Table 1: Results of the additional heat load and ambient conditions

| Item | Original Design | Original Design with Additional Heat Load |
| --- | --- | --- |
| Heat Load | 53,200 BTU/Min | 95,250 BTU/Min |
| Design Basis Temperature | 108 Deg F | 91 Deg F |
| Fluid | 50% Propylene-Glycol / 50% Water | 50% Propylene-Glycol / 50% Water |
| Fluid Flow Rate | 952 GPM | 952 GPM |
| Fluid Inlet Temperature | 136 Deg F | 141 Deg F |
| Fluid Outlet Temperature | 128 Deg F | 128 Deg F |
| Fan Redundancy | 3 x 50% | 3 x 50% |

The major additional components for the cooling water system are:

- Temperature Regulating Valve – Robert Shaw

- Atomizing Air Heat Exchanger – ITT Standard

- Purge Air Heat Exchanger – ITT Standard

The original cooling water piping supplied with the unit will be modified to incorporate the atomizing air heat exchanger and the purge air heat exchanger. A temperature control valve will be added at the atomizing air heat exchanger that controls the atomizing air outlet temperature by passing water to or around the heat exchanger.

Combustion System:

The dual fuel modification utilizes combustion technology that is based on GE’s DLN 1.0 system. In order to determine design flow rates, ProEnergy evaluated new dual fuel primary and secondary fuel nozzles. Based on this information, ProEnergy modified existing “gas only” fuel nozzles to meet similar performance requirements. The original “gas only” fuel nozzles were removed directly from the unit while in storage.

The materials utilized to modify the nozzles were purchased directly from vendors that provide similar material to GE. ProEnergy utilized industry standards and general practices to modify and confirm the nozzles prior to shipping them to the project site.

After the modifications to the nozzles were completed, ProEnergy performed flow tests to confirm the nozzles were performing according to the design specifications. Below are the specifications for the flow tests performed on the nozzles.

Specifications for Primary Fuel Nozzles (End Covers)

|  | Atomizing Air (in2) (see note 1) | Gas Fuel (in2) (see note 1) | Water (lbs/hr) (see note 2) | Liquid Fuel (lbs/hr) (see note 2) |
| --- | --- | --- | --- | --- |
| Maximum | 0.1224 | 0.3468 | 4549.2 | 1847.22 |
| Nominal | 0.1200 | 0.3400 | 4460.0 | 1811.00 |
| Minimum | 0.1176 | 0.3332 | 4370.8 | 1774.78 |

Note 1) Flow test performed with fluid at 1.25PR

Note 2) Flow test performed with fluid at 100 psig

Specifications for Secondary Fuel Nozzles

|  | Secondary Gas (in2) (see note 1) | Tertiary Gas (in2) (see note 1) | Water (lbs/hr) (see note 2) | Liquid Fuel (lbs/hr) (see note 2) |
| --- | --- | --- | --- | --- |
| Maximum | 0.1520 | 0.2805 | 1592.0 | 1747.0 |
| Nominal | 0.1490 | 0.2750 | 1561.0 | 1713.0 |
| Minimum | 0.1460 | 0.2695 | 1530.0 | 1679.0 |

Note 1) Flow test performed with fluid at 1.25PR

Note 2) Flow test performed with fluid at 100 psig

The combustion liner and transition piece will remain the same as the gas only configuration. The combustion liner should be coated with Thermal Barrier Coating (TBC) which is typical in the gas only configuration.

The modified primary and secondary fuel nozzles will be installed with new gaskets. The piping and tubing to the fuel nozzles will be installed to fit without any interference and optimized for maintenance outages.

Cooling & Sealing Air System:

The existing cooling and sealing air system will be tapped to supply compressor discharge air to the atomizing air system. This modification includes several spools of piping, an isolation valve for water washing the compressor, several flexible hoses, and low point drains to remove any potentially trapped water from the system. Modifications to these systems are typical and standard design.

The compressor discharge casing will also be tapped to provide an air source to operate the false start drain valves. Compressed air from the compressor discharge casing is the typical source to operate these valves.

Liquid Fuel Forwarding System

The liquid fuel forwarding system is designed to receive fuel from a storage tank and forward to the liquid fuel metering spool at 70 psi and a maximum flow rate of 150 gpm. The forwarding skid utilizes two 100% pumps and has a duplex strainer at the suction to the pumps.  A back pressure regulating valve controls the outlet header pressure by bypassing fuel back to the storage tank. A pressure switch is located on the outlet header of the pump and is designed to provide feedback to the customer’s control system or the turbine control system to start the standby pump as pressure decays in the header. A vacuum switch is utilized at the suction header to the pumps to protect the pump.

The skid is designed with check valves at the outlet of each pump and utilizes “fire safe” butterfly valves so each pump can be isolated for maintenance requirements.

The fuel forwarding pump skid base is equipped with a base drain to ensure that any fuel or oily water can be captured. The customer can pipe the skid drain into the plant oily water separator system. The fuel forwarding pump base is painted with an epoxy “shark grip” paint to minimize slippery conditions for personnel. The fuel forwarding skid is an open base design (not enclosed) with two electrical junction boxes for interface connections. One junction box is for the power supply and the other junction box is for the instrumentation signals. The skid also has a local gauge panel.

Demineralized Water Forwarding System

The demineralized water forwarding system is designed to receive demineralized water from a storage tank and forward to the water injection skid at 65 psi and a maximum flow rate of 150 gpm. The forwarding skid utilizes two 100% pumps.  A back pressure regulating valve controls the outlet header pressure by bypassing fuel back to the storage tank. A pressure switch is located on the outlet header of the pumps and is designed to provide feedback to the customer’s control system or the turbine control system to start the standby pump as pressure decays.

The skid is designed with check valves at the outlet of each pump and utilizes butterfly valves so each pump can be isolated for maintenance requirements. A ball valve is installed at the inlet for a good positive shut off.

The demineralized water forwarding pump skid base is equipped with a base drain to ensure that any demineralized water can be captured. The customer can pipe the skid drain into the plant waste water system. The demineralized water forwarding pump base is painted with an epoxy “shark grip” paint to minimize slippery conditions for personnel and is resistant to the corrosiveness of the demineralized water.

The demineralized water forwarding skid is an open base design (not enclosed) with two electrical junction boxes for interface connections. One junction box is for the power supply and the other junction box is for the instrumentation signals. The skid also has a local gauge panel.

Because of the corrosiveness of the demineralized water, all piping on the skid, valves, tubing, instrumentation and the pump are made of stainless steel.

Water Injection System

A complete water injection system will be added to the unit. The system added to the turbine compartment will include a stainless steel water distribution header and check valves at each fuel nozzle (primary and secondary).

A water injection skid will be added adjacent to turbine compartment. The water injection skid will receive demineralized water from the forwarding skid, filter the water, and boost the water pressure. The water injection pump utilizes a variable frequency drive on the motor and a flow meter for feedback to the control system. The skid also has a solenoid stop valve at the output of the skid for protection and control. The solenoid stop valve will utilize instrument air as a motive force to open the valve. Below are the major components for the water injection system.

- Check Valves – Jensen Aircraft Systems

- High Pressure Pump  & Motor– Sunflo

- Duplex Filter with Transfer Valve – Hilco Hilliard

- Variable Speed Drive – Fuji Drives

- Flow Meter – Flow Technology

- Stop Valve – CR Tec

The water injection skid design was based on an existing skid. The water injection skid for Margarita was developed utilizing the components that had been proven in similar applications. The piping and piping components will deliver the same flow and pressure as specified on similar systems developed by GE.

The water injection skid is an enclosed skid with insulation on the roof and walls. The insulation is secured with stainless steel perforated plate that will not corrode. The insulation and perforated plate also act as a noise attenuator.

The skid base is painted with an epoxy “shark grip” paint to minimize slippery conditions for personnel and is resistant to the corrosiveness of the demineralized water.

The skid utilizes an air conditioning unit to cool the compartment.

Because of the corrosiveness of the demineralized water, all piping on the skid, valves, tubing, instrumentation and pump are made of stainless steel.

Gas Fuel System

The existing gas fuel module will be modified to include purge air on the primary, secondary, and transfer gas headers. A vent valve will also be added to vent any gas that would accumulate between the two block valves.

This is a standard modification provided by a vendor of the gas fuel module and will include piping, Fisher purge and vent valves, insulation blankets, and a pressure switch to monitor gas pressure between the two purge valves. The purge and vent valves will utilize instrument air that is being utilized by other valves on the skid.

All devices, conduit, and junction boxes that will be added to the skid will be explosion proof.

Design Considerations

Electrical Systems

The electrical scope of work on the dual fuel project is relatively small. The only electrical modification to the unit is the addition of an atomizing air booster compressor motor. Because there are no spares available in the PECC, ProEnergy will supply a breaker that will be installed in the PECC. The design calculations for this breaker will be provided in the electrical calculations document. The breaker for the atomizing air booster compressor will be controlled by the turbine control system. The software and the wiring to control the breaker will be part of ProEnergy’s scope of work.

The off base equipment that will be added to provide dual fuel capability is identified in the table below. The customer is required to provide switchgear (breakers), cable and conduit from the breakers to the skids, and for breaker control (to the DCS or turbine control panel).

For the fuel forwarding and demineralized water forwarding pump motors, breaker controls will need to be provided (in the turbine or DCS control system) that will open or close the breaker as required. The fuel forwarding and demineralized water forwarding skids are equipped with a pressure switch on the outlet of the pump that will close on a low pressure event. Control logic will be developed to send a signal to the standby pump motor breaker to close.  The pump skids are also equipped with a pressure switch on pump suction to ensure there is sufficient head pressure to the pump and protect the pump from damage.

The water injection skids will utilize power directly from a breaker and will not require breaker controls. The water injection skids are equipped with a transformer to provide 240V and 120V on the skids as required.

Below is a list of the Equipment that will require switchgear (breakers).

| Location | Device Name | Amps - Full Load (see note 1) | Voltage |
| --- | --- | --- | --- |
| Fuel Forwarding (unit 1) | 88 FD-1 | 25.0 | 480 V |
| Fuel Forwarding (unit 1) | 88FD-2 | 25.0 | 480 V |
| Fuel Forwarding (unit 2) | 88FD-1 | 25.0 | 480 V |
| Fuel Forwarding (unit 2) | 88FD-2 | 25.0 | 480 V |
| Demineralized Water Forwarding (unit 1) | 88WF-1 | 18.0 | 480 V |
| Demineralized Water Forwarding (unit 1) | 88WF-2 | 18.0 | 480 V |
| Demineralized Water Forwarding (unit 2) | 88WF-1 | 18.0 | 480 V |
| Demineralized Water Forwarding (unit 2) | 88WF-2 | 18.0 | 480 V |
| Water Injection Skid | Multiple | 80.0 | 480 V |
| Water Injection Skid | Multiple | 80.0 | 480 V |

Note 1:  The liquid fuel forwarding and demineralized water forwarding amp loads reflect the motor sizes submitted to customer for approval.

Instrumentation

The Device Summary originally supplied with the unit has been modified to include devices added for the dual fuel modification.  The modified device summary (drawing AGM-02-0204-PLA-M-0046) has all of the devices identified with settings and specifications.

Additional junction boxes, pull boxes, and conduit installed will be minimum of NEMA 4 rating. The conduit from the devices to junction boxes will be rigid galvanized. Flexible conduit and Seal Tite connections will be used at the device to tie into the rigid conduit. Several existing junction boxes on the turbine and accessory bases will be utilized.

Wire / cable utilized for the dual fuel modification will be to GE specifications and will have a minimum temperature rating of 90 deg C.

Several instruments that will be added on the accessory base will tie directly into existing conduit runs as per typical dual fuel units. Any additional conduit that will be installed will not interfere with existing equipment or future modifications. The cable installed will be per industry standards and terminated in existing junction boxes. The original equipment drawings will be modified to reflect the additional terminations and cables.

Turbine Control System

The turbine control sequencing and logic required for the dual fuel system have been modified or added as required. The control system operating philosophy and standardization is based on GE design principles and operating requirements to support turbine operation with similar combustion systems utilizing water injection for NOx control. The existing Mark V control system will need to be modified to support the additional inputs and outputs required for the dual fuel modification.

The turbine control system will be able to start and control the turbine on liquid fuel or gas fuel. The software and sequencing that will be added will allow the unit to transfer from liquid to gas fuel while synchronized to the grid. Confirmation of this feature will be demonstrated during the commissioning of the unit.

Additional cables and wiring will be required to connect the new devices and equipment to the turbine control system. The Cable List Drawing issued by GE specifically for the unit will be modified to include the additional cables required to implement the dual fuel modification. The Cable List Drawing will be issued as a Product of Engineering.

The additional cables and wires will connect the field devices to the turbine control panel. The Interconnection Diagram issued by GE specifically for the unit will be modified to include the additional field devices, connection points in the field, and the termination location in the control panel. The Interconnection Diagram will be issued as a Product of Engineering.

Civil Interface

The majority of the dual fuel modification will occur on the accessory and turbine bases. However there are several civil interfaces that need to be considered. The liquid fuel forwarding, demineralized water forwarding, and water injection skids will require foundations to be placed. The customer’s scope of work is to design and install these foundations.

The general arrangement drawings of the skids outline the skid dimensions, anchor bolt hole locations, and weights. The skids mentioned above will not experience any dynamic loads and can be anchored to the foundation with anchor bolts that are drilled and set in place with epoxy.

Environmental

There are several key interfaces associated with the dual fuel modification that provide protection for the environment. Below is a summary of these interfaces that should be considered for the plant design.

- The Fuel Forwarding Skids have an extended lip above the surface of the base and a base drain to capture any fuel leaks or spills. The base drain should be tied into the plant oily waste drain system to avoid any soil contamination

- The Demineralized Water Forwarding Skids also have skid containment with a base drain in order to capture demineralized water that can corrode carbon steel and concrete. The base drain should be tied into the plant waste water system.

- The Water Injection Skid is designed with a base drain and should also be tied into the plant waste water system.

- The False Start Drain System includes drains at three points on the turbine. These drains should be tied into the plant waste water and oily water system to capture waste water during water wash events, and to the oily waste drain for false fire events to capture waste fuel. Refer to Drawing AGM-02-0204-PLA-M-0021.

- The accessory base has a fuel drain sump to capture any liquid fuel drained from points in the system including fuel filters, relief valve blow down, and low point drains. This drain sump should be tied into the plant waste oil system.

Specific locations of these drain points are identified on the skid general arrangement drawings and on the Package Piping Connection Drawing AGM-02-0204-PLA-M-0004.

Mechanical Scope

Piping, tubing, valves, fittings, and equipment will be installed per industry standards and practices. The piping on all systems is fabricated per ASME B31.1. All welders performing welds on the piping and supports have current welding certifications that match the scope of work being performed.

Piping provided on for the modification have been cleaned and packaged for shipment. Prior to installation, the piping will be blown down to confirm no foreign material has contaminated the piping spools. After the piping has been fit up to the unit, the systems will be opened up and flushed to remove any contamination caused by the field fabrication works.

The equipment will be installed per the vendor or manufactures literature. Rotating pumps and valves will be installed in a strain free condition. Pumps and motors will be aligned according to the vendor specifications for the pumps and coupling manufacturers. All installation details will be provided to the customer.

Seismic requirements were not considered during the development of the dual fuel modification package. This decision was made based on the equipment to be provided would be installed directly on the accessory and turbine base. The forwarding skids and water injection skids did not require such evaluation and were being installed on Customer provided foundations.

Other

The installation of the dual fuel modification package will be directed and overseen by Mechanical and Controls Technical Advisors that have previously installed this modification on other units. The Technical Advisors will collect data and monitor the work of the craftsmen to ensure the systems are installed and commissioned properly. A turn over package will be issued to the Customer for the dual fuel modification scope of work.

The Technical Advisors will make any mark-ups to the drawings to reflect any “as built” deviations. A final set of drawings will be issued to the customer to reflect the installed systems.

The Controls Technical Advisor will work with the Customer or Installation contractor to modify, adjust, or develop any interfaces for the dual fuel systems.