Project Description – Dual Fuel Modification of 7EA Gas Turbine

Introduction:

ProEnergy has developed a Dual Fuel Modification Package to be installed on GE 7EA Gas Turbines originally built by the OEM as “Gas Only” units. This modification, when applied to a “Gas Only” unit, will allow it to start and operate on natural gas or distillate fuel.  The Dual Fuel Modification Package was developed through evaluations of several existing GE 7EA dual fuel units. ProEnergy developed systems for this package that provide similar functionality and are comprised of equipment that has been proven in the same application.

ProEnergy has developed these systems to fit into the existing turbine and accessory packages so that they will not interfere with existing equipment or future modifications. ProEnergy has performed engineering evaluations for new equipment that have not been proven in this application.

ProEnergy used industry standards and general practices to fabricate and assemble equipment for the dual fuel modification. ProEnergy followed ASME pressure and piping codes for fabrication works.

Derwick / EDC supplied drawings and documentation to ProEnergy specifically for the units being modified. These documents included all drawings, specifications, and documentation for the equipment that was issued by the original OEM and their sub vendors.  These drawings were evaluated and modified to reflect the duel fuel modification that will be applied to the units.

The turbine unit serial numbers that will be modified to dual fuel are 298034 and 298035 manufactured by General Electric.

Location

The procurement, fabrication, and packaging of the equipment required to perform the dual fuel modification on the units will be performed in Sedalia, Missouri, USA. All of the material required will be consolidated and crated for shipment.

The project site where the units will be installed and the dual fuel modification implemented is located Margarita Island, Venezuela.

Scope of Work

ProEnergy performed various take offs of existing dual fuel systems to develop the dual fuel modification package.  Below is a list of existing systems on the equipment that will be modified to incorporate the dual fuel modification.

- Lube Oil System – Refer to Drawing AGM-02-0204-PLA-P-0061

The lube oil system will be tapped to supply the main atomizing air compressor with lubricating oil. The piping and connection points in the lube oil tank for the feed and drain of the main atomizing air compressor are existing.

- Hydraulic Oil System  (no change to original drawing issued for unit)

The hydraulic oil system will be tapped to supply hydraulic oil to the liquid fuel bypass / control valve for actuation / control, and to the isolation valve on the flow divider skid to actuate the valve. The piping and connection points for these two pieces of equipment are in the lube oil tank and will provide the feed and drain to these valves.

- Trip Oil System – Refer to Drawing AGM-02-0204-PLA-P-0050

A trip oil solenoid valve will be added to the trip oil system for the liquid fuel stop valve. The stop valve will provide primary protection for the unit. When the trip oil solenoid de-energizes, trip oil pressure to the stop valve will be lost and the spring loaded stop valve will close and stop the flow of liquid fuel.  Pressure gauges and switches will be added in order to monitor the pressure of the trip oil system for the stop valve.

- Cooling Water System – Refer to Drawing AGM-02-0204-PLA-P-0051

The existing cooling water system on the turbine generator will be modified to include two additional heat loads. The atomizing air heat exchanger and purge air heat exchanger will create an additional 42,050 BTU/Min heat load to the system for a total of 95,250 BTU/Min.

The atomizing air heat exchanger is a shell and tube design. The atomizing air heat exchanger will remove heat from the compressor discharge air that is supplied to the inlet of the main atomizing air compressor.  A temperature control / bypass valve will be added on the water side of the heat exchanger and will control the outlet temperature of the atomizing air by allowing more or less water to the heat exchanger.

The purge air heat exchanger is also a shell and tube design. The purge air heat exchanger will remove heat from the air leaving the atomizing air compressor before it enters into the purge air system. There is no control valve on the water side of this system.

The existing cooling water module supplied with the unit was evaluated for the additional heat load and for the new design conditions at Margarita Island. This evaluation was performed by GEA, the original designer and provider of the cooling water module.

Using the new design basis below, the results of the cooling water system evaluation are shown in Table 1.

- Maximum Ambient Temperature:  32 Deg C (91.0 deg F)

- Maximum Relative Humidity:  90%

- Altitude:  Sea Level

Table 1: Results of the additional heat load and ambient conditions

| Item | Original Design | Original Design with Additional Heat Load |
| --- | --- | --- |
| Heat Load | 53,200 BTU/Min | 95,250 BTU/Min |
| Design Basis Temperature | 108 Deg F | 91 Deg F |
| Fluid | 50% Propylene-Glycol / 50% Water | 50% Propylene-Glycol / 50% Water |
| Fluid Flow Rate | 952 GPM | 952 GPM |
| Fluid Inlet Temperature | 136 Deg F | 141 Deg F |
| Fluid Outlet Temperature | 128 Deg F | 128 Deg F |
| Fan Redundancy | 3 x 50% | 3 x 50% |

The major additional components for the cooling water system are:

a) Temperature Regulating Valve – Robert Shaw; Provides temperature control to the atomizing air by diverting cooling water to or around the atomizing air heat exchanger

b) Atomizing Air Heat Exchanger – ITT Standard; Shell and Tube heat exchanger that removes heat from the air supplied by the compressor discharge prior to entering the atomizing air compressor

c) Purge Air Heat Exchanger – ITT Standard; Shell and Tube heat exchanger that removes heat from the atomizing air prior to entering the purge air system

The original cooling water piping supplied with the unit will be modified to incorporate the atomizing air heat exchanger and the purge air heat exchanger. A temperature control valve will be added at the atomizing air heat exchanger which will control the atomizing air outlet temperature by passing water to or around the heat exchanger.

- Cooling and Sealing Air System – Refer to Drawing AGM-02-0204-PLA-P-0049

The Cooling and Sealing Air System will be tapped at three locations to provide a source of air. The compressor discharge casing will be tapped to supply air to the atomizing air system.

The compressor discharge casing will also be tapped to supply control air to three air operated valves on the false start drain system.

The compressor discharge air will also be used as a reference pressure for the transmitters in the purge protection panel that will be added.

Modifications that will be performed to this system are typical and standard for dual fuel applications. All piping, tubing, and fittings will be supplied.

- Gas Fuel System – Refer to Drawing AGM-02-0204-PLA-P-0052

The gas fuel system (gas fuel module) will be modified to add purge valves to the primary gas header and a vent valve to vent any residual gas between the two added purge valves. The existing instrument air header in the skid will be tapped to supply air for actuation for the valves.

A set of pressure switches will be added to the gas fuel piping to provide feedback to the control system for operation of these valves.

This is a standard modification this will be provided by a vendor of the gas fuel module. This modification kit and will include piping, Fisher purge and vent valves, insulation blankets, and a pressure switch to monitor gas pressure between the two purge valves. The purge and vent valves will utilize instrument air that is already piped to the skid.

All devices, conduit, and junction boxes that will be added to the skid will be explosion proof.

- Combustion System – Refer to Drawing AGM-02-0204-

The dual fuel modification utilizes combustion technology that is based on GE’s DLN 1.0 system.  The original configuration of the fuel system for the Margarita Units was gas fuel.

The “gas only” primary and second fuel nozzles were removed from the Margarita Gas Turbines while in storage in New Jersey, USA and modified for dual fuel application in the ProEnergy Shop.

In order to determine design flow rates, ProEnergy evaluated new dual fuel primary and secondary fuel nozzles and collected baseline flow data. Based on this information, ProEnergy modified the existing “gas only” fuel nozzles to meet similar performance requirements.

The materials utilized to modify the nozzles were purchased directly from vendors that provide similar material to GE. ProEnergy utilized industry standards and general practices to modify and confirm the nozzles prior to shipping them to the project site.

After the modifications to the nozzles were completed, ProEnergy performed flow tests to confirm the nozzles were performing according to the design specifications.

The combustion liners, cross fire tubes, and transition pieces will remain the same as the gas only configuration. The combustion liner should be coated with Thermal Barrier Coating (TBC) which is typical in the gas only configuration.

The modified primary and secondary fuel nozzles will be installed with new gaskets. The piping and tubing to the fuel nozzles will be installed to fit without any interference and optimized for maintenance outages.

- Turbine Control System – Refer to Drawing AGM-02-0204-PLA-V-0003

The turbine control sequencing and logic required for the dual fuel system have been modified or added as required. The control system operating philosophy and standardization is based on GE design principles and operating requirements to support turbine operation with similar combustion systems utilizing water injection for NOx control. The existing Mark V control system will need to be modified / upgraded to support the additional inputs and outputs required for the dual fuel modification.

The turbine control system will be able to start and control the turbine on liquid fuel or gas fuel. The software and sequencing that will be added will allow the unit to transfer from liquid to gas fuel while synchronized to the grid. Confirmation of this feature will be demonstrated during the commissioning of the unit.

Additional cables and wiring will be required to connect the new devices and equipment to the turbine control system. The unit specific Cable List Drawing issued by GE for the unit will be modified to include the additional cables required to implement the dual fuel modification. The Cable List Drawing will be issued as a Product of Engineering. (Refer to Drawing AGM-02-0204-PLA-E-0006)

The additional cables and wires will connect the field devices to the turbine control panel. The unit specific Interconnection Diagram and Turbine Connection Diagram issued by GE will be modified to include the additional field devices, connection points in the field, and the termination location in the control panel. The Interconnection Diagram and Turbine Connection Diagram will be issued as a Product of Engineering. (Refer to Drawing AGM-02-0204-PLA-E-0058 for the Revised Interconnection Diagram and AGM-02-0204-PLA-E-007 for the Revised Turbine Connection Diagram).

The following is a general list of the software adjustments required as part of the dual fuel modification:

1-Add variable speed control time constant - one for liquid / one for gas

2- Add variable speed acceleration control gain constant – one for liquid / one for gas

3- Add multiple variable speed pickup set points for liquid or gas fire speed

4- Add multiple variable speed drop out set points for liquid or gas fire speed

5- Upgrade FSR acceleration block from single to dual fuel

6- Add liquid fuel variable acceleration curve constants

7- Add two extra acceleration speed set point blocks for liquid fuel

8- Modify FSNL MIN FSR Calibration Block to include liquid array

9- Modify load rejection block to include liquid fuel tuning constants

10-Add liquid fuel protection shut down to lower FSR logic

11-Add liquid fuel transfer cross function block and tie into raise / lower FSR logic

12- Modify mode selection blocks to include liquid fuel

13- Add liquid / gas selection to cable remove interface

14- Add liquid fuel trip relay condition monitoring to master protective sequence / start inhibit 15- Add gas control valve fault auto transfer inhibit

16- Add liquid control valve fault auto transfer inhibit

17- Add liquid fuel scaling sequencing for values for HMI display

18- Add water injection scaling sequencing for values for HMI display

19- Add liquid fuel servo calibration block – add to start-up lock out

20- Add water injection to liquid fuel ratio calculation bloc and constants

21- Tie in IBH Control offset for liquid fuel transfer

22- Split FSR control block to create two FSR valves per fuel, tie into fuel transfer pre-fill calculation block

23- Add liquid fuel to totalizer logic

24- Add gas fuel purge logic

25- Add liquid fuel purge logic

26- Add liquid fuel forwarding pump logic

27- Add demineralized water forwarding pump logic

28- Add second shutdown curve for liquid fuel

29- Add 88AB-1 Booster Compressor control logic

30- Add liquid fuel interlocks to “start check” screen

31- Add limited bypasses for gas fuel start checks when liquid is selected

32- Add excessive liquid fuel flow protection

33- Add four separate part load firing curves; two for liquid fuel, and two for gas fuel (CPR/DWATT)

34- Modify IBH schedule to have separate curves depending on fuel selected

35- Add secondary liquid fuel control block

36- Add primary liquid fuel passive / active mode temperature switch

37- Add secondary liquid fuel passive / active mode temperature switch

38- Add active purge back pressure reduction sweep function for liquid fuel OP / Transfer

39- Add exhaust temperature spread liquid fuel offset block

40- Add water injection exhaust mass flow offset calculation block

41- Add liquid fuel flow divider / bypass valve flow controller

42- Add liquid fuel pump clutch logic

43- Add high pressure pump low suction pressure protection logic

44- Add liquid fuel trip oil monitoring and alarm circuit

45- Add atomizing air temperature monitoring and control circuit

46- Add atomizing air pressure monitoring and control block

47- Add water injection / secondary purge transfer to gas block

48- Add liquid fuel bas load curves (CPR/DWATT)

49- Add emergency transfer to liquid fuel block

50- Add emergency transfer to gas block

51- Add liquid fuel signals to trip capture blocks

52- Modify HMI screen to add multi fuel selection

52- Add liquid fuel control screen

53- Add water injection control screen

54- Update alarm list for liquid fuel

55- Update ENUM.DAT files to include liquid fuel status

56- Update IO.DAT files with liquid fuel inputs & outputs

57- Segment the control sequence in eight sections rather than five to allow faster scan rate on Mark VI

58- Re-allocate memory for larger sequence section and reduce long term trend space

59-Update LONGNAME.DAT file

60- Update CONST_Q.SRC file

61- Update ALARM.DAT file for liquid fuel

62- Update IO.CFG file for new liquid fuel devices

63- Update MK5MAKE and down load all data

64-Update TIMERS screen on HMI to include totalizers

Below is a description of new systems that will be added to the turbine generator to configure the unit for dual fuel operation.

- Liquid Fuel System (turbine generator) – Refer to Drawing AGM-02-0204-PLA-P-0048

A complete liquid fuel system will be added to the unit. It will include all hardware and equipment to measure, control, filter, and pump the liquid fuel from the suction of the treated fuel tank to the fuel nozzles of the turbine for combustion.

A complete liquid fuel system will be added to the Margarita unit. Several of the controlled components that will be added will be connected into the existing hydraulic and lube oil systems. The system will include several instruments and devices which will provide the input and feedback signals to the control system.  The design of this system is based other similar systems and utilizes equipment that has been proven in equivalent applications. Below are several of the major components that will be utilized.

- Liquid Fuel Duplex Filter and Transfer Valve – Manufactured by Hilco / Hilliard; Final filtration for the liquid fuel prior to being consumed in the unit. The filter cartridges can provide filtration for one micron contamination.

- Liquid Fuel Stop Valve with limit switch feedback– Young & Franklin; Provides the primary source of protection for the gas turbine

- Main Fuel Pump – Colfax / IMO; Provides high pressure fuel to the fuel nozzles for combustion

- Liquid Fuel By-pass Valve with servo control and LVDT feedback – Young & Franklin; Provides direct control of fuel being consumed in the gas turbine and is controlled by the turbine control system

- Fuel Pump Solenoid Clutch  – Carlyle Johnson; Clutch is energized by the turbine control system to start the main fuel pump

- Flow Divider with magnetic speed pick-ups  – Roper Industries; Distributes flow to the nozzles providing feedback to the turbine control system

- Isolation Valve with limit switch feedback– Parker Hannifin Corporation; Isolates fuel to the secondary nozzles with position feedback to the turbine control system

- Solenoid Stop Valve – Ruggles-Klingemann Mfg.; Trip oil solenoid for the main fuel stop valve

- False Start Drain Valves – RG Laurence; Air operated drain valves for residual water from the compressor water wash and liquid fuel drain for false fires

- Atomizing Air System – Refer to Drawing AGM-02-0204-PLA-P-0053

A complete atomizing air system will be added to the Margarita unit. Several of the components that will be added will be connected into the existing lube oil, control air, and cooling water systems. The system will include several instruments that will be added which will provide the input and feedback signals to the control system.

The design of this system is based other similar systems and utilizes equipment that has been proven in equivalent applications. Below are several of the major components that will be utilized.

- Atomizing Air Heat Exchanger – ITT Standard; Shell and Tube heat exchanger that will remove heat from the air supplied by the compressor discharge prior to entering the atomizing air compressor

- Bypass Control Valves – Contromatics; Air operated butterfly control valves that controls atomizing air to the booster compressor and to the combustion system

- Atomizing Air Booster Compressor  & motor– Gardner Denver; Positive displacement blower that provides a source of atomizing air to the combustion system during start-up of the turbine

- Atomizing Air Check Valves – Meuller “Chexter Check”; Provides back flow protection in the atomizing air piping

- Main Atomizing Air Compressor – Atlas Copco; Positive displacement compressor that provides the primary source of atomizing air to the combustion system during operation

- Atomizing Air Filter – Hilco Hilliard; Provides filtration at the suction of the main atomizing air compressor

- Flexible Hoses – MicroFlex; Flexible metal hoses designed and fabricated specifically for the atomizing air system

One of the new items that will be incorporated into the design for Margarita is the motor starter and breaker for the atomizing air booster compressor. The breaker / motor starter will be installed in the PECC and controlled by the turbine control system.  See design details in the technical specifications.

The atomizing air system piping was designed and fabricated according to existing systems. All of the piping is fabricated with stainless steel pipe to eliminate any sources of contamination.

- Purge Air System – Refer to Drawing AGM-02-0204-PLA-P-0054

The existing purge air system for the gas fuel system will be added.  A purge air heat exchanger will be added to cool the purge air, a purge panel with solenoid valves to control air flow to the three headers in the turbine compartment; one for the primary fuel nozzles, one for the secondary fuel nozzles, and one for water injection. A purge protection panel will be added to the roof of the turbine compartment to monitor pressures in the three headers. These pressure transmitters will provide feedback to the control system to alert if a problem arises. The purge air system will include several other instruments which will provide the input and feedback signals to the control system. The design of this system is based other similar systems and utilizes equipment that has been proven in equivalent applications. Below are several of the major components that will be utilized.

- Purge Air Heat Exchanger – ITT Standard; Shell and Tube Heat Exchanger that removed heat from the atomizing air prior to entering the purge air system

- Purge Valves – 3 way – Jensen Aircraft Systems; Diverts purge air to the liquid fuel and water injection passages in the fuel nozzles

- Check Valves –  Jensen Aircraft Systems; Provides reverse flow protection in the water injection check valves

- Purge Valves (air operated)– Flowtek; Air operated ball valves that control purge air to the purge air headers in the turbine compartment

The piping and tubing for this system is fabricated with stainless steel to maintain cleanliness of the air to the fuel nozzles. The connections between the purge air headers to the nozzles are made with tubing connections to ease removal and reassembly during maintenance events.

Demineralized Water Forwarding– Refer to Drawing AGM-02-0204-PLA-P-0047

The demineralized water forwarding system is designed to receive demineralized water from a storage tank and forward to the water injection skid at 65 psi and a maximum flow rate of 150 gpm. The forwarding skid utilizes two 100% pumps.  A back pressure regulating valve controls the outlet header pressure by bypassing fuel back to the storage tank. A pressure switch is located on the outlet header of the pumps and is designed to provide feedback to the customer’s control system or the turbine control system to start the standby pump as pressure decays.

The skid is designed with check valves at the outlet of each pump and utilizes butterfly valves so each pump can be isolated for maintenance requirements. A ball valve is installed at the inlet for a good positive shut off.

The demineralized water forwarding pump skid base is equipped with a base drain to ensure that any demineralized water can be captured. The customer can pipe the skid drain into the plant waste water system. The demineralized water forwarding pump base is painted with an epoxy “shark grip” paint to minimize slippery conditions for personnel and is resistant to the corrosiveness of the demineralized water.

The demineralized water forwarding skid is an open base design (not enclosed) with two electrical junction boxes for interface connections. One junction box is for the power supply and the other junction box is for the instrumentation signals. The skid also has a local gauge panel.

Because of the corrosiveness of the demineralized water, all piping on the skid, valves, tubing, instrumentation and the pump are made of stainless steel.

Reference Drawings:

Assembly Drawing – Demin Water Forwarding: 		AGM-02-0204-PLA-M-0037

General Arrangement – Demin Water Forwarding:	AGM-02-0204-PLA-M-0038

Electrical – Demin Water Forwarding:			AGM-02-0204-PLA-E-0040

Water Injection System – Refer to Drawing AGM-02-0204-PLA-P-0047

A complete water injection system will be added to the unit. The system added to the turbine compartment will include a stainless steel water distribution header and check valves at each fuel nozzle (primary and secondary).

A water injection skid will be added adjacent to turbine compartment. The water injection skid will receive demineralized water from the forwarding skid, filter the water, and boost the water pressure. The water injection pump utilizes a variable frequency drive on the motor and a flow meter for feedback to the control system. The skid also has a solenoid stop valve at the output of the skid for protection and control. The solenoid stop valve will utilize instrument air as a motive force to open the valve. Below are the major components for the water injection system.

- Check Valves – Jensen Aircraft Systems; Provides flow protection for the injection water

- High Pressure Pump  & Motor– Sunflo; Provides variable flow directly to the combustion system utilizing a variable frequency drive controller

- Duplex Filter with Transfer Valve – Hilco Hilliard; Provides final filtration of the water being consumed in the combustion turbine

- Variable Speed Drive – Fuji Drives; Provides variable frequency drive to the water injection pump motor, it is controlled by the gas turbine control system

- Flow Meter – Flow Technology; Provides feedback to the turbine control system for water injection flow rate

- Stop Valve – CR Tec; Provides protection of the unit for injection water

The water injection skid design was based on an existing skid. The water injection skid for Margarita was developed utilizing the components that had been proven in similar applications. The piping and piping components will deliver the same flow and pressure as specified on similar systems developed by GE.

The water injection skid is an enclosed skid with acoustical insulation on the roof and walls. The insulation is secured with stainless steel perforated plate that will not corrode. The insulation and perforated plate also act as a noise attenuator.

The skid base is painted with an epoxy “shark grip” paint to minimize slippery conditions for personnel and is resistant to the corrosiveness of the demineralized water.

The skid utilizes an air conditioning unit to cool the compartment.

Because of the corrosiveness of the demineralized water, all piping on the skid, valves, tubing, instrumentation and pump are made of stainless steel.

Reference Drawings:

Mechanical – Water Injection: 				AGM-02-0204-PLA-M-0044

General Arrangement – Water Injection:		AGM-02-0204-PLA-M-0041

Electrical – Water Injection:				AGM-02-0204-PLA-E-0043

Liquid Fuel Forwarding System – Refer to Drawing: AGM-02-0204-PLA-M-0048

The liquid fuel forwarding system is designed to receive fuel from a storage tank and forward to the liquid fuel metering spool at 70 psi and a maximum flow rate of 150 gpm. The forwarding skid utilizes two 100% pumps and has a duplex strainer at the suction to the pumps.  A back pressure regulating valve controls the outlet header pressure by bypassing fuel back to the storage tank. A pressure switch is located on the outlet header of the pump and is designed to provide feedback to the customer’s control system or the turbine control system to start the standby pump as pressure decays in the header. A vacuum switch is utilized at the suction header to the pumps to protect the pump.

The skid is designed with check valves at the outlet of each pump and utilizes “fire safe” butterfly valves so each pump can be isolated for maintenance requirements.

The fuel forwarding pump skid base is equipped with a base drain to ensure that any fuel or oily water can be captured. The customer can pipe the skid drain into the plant oily water separator system. The fuel forwarding pump base is painted with an epoxy “shark grip” paint to minimize slippery conditions for personnel. The fuel forwarding skid is an open base design (not enclosed) with two electrical junction boxes for interface connections. One junction box is for the power supply and the other junction box is for the instrumentation signals. The skid also has a local gauge panel.

Reference Drawings:

Assembly – Liquid Fuel Forwarding: 			AGM-02-0204-PLA-M-0033

General Arrangement – Liquid Fuel Forwarding:		AGM-02-0204-PLA-M-0034

Electrical – Liquid Fuel Forwarding:			AGM-02-0204-PLA-E-0036

Liquid Fuel Management Spool:  Refer to Drawing: AGM-02-0204-PLA-M-0048

The Fuel Management Spool was added as an additional feature to the liquid fuel system. A flow meter is included in the fuel metering spool and has a totalizing feature that ties directly into the turbine control system. A bypass around the flow meter is provided in the case of maintenance requirements on the meter.

The spool also includes a solenoid stop valve for secondary protection for the turbine and a pressure control valve to eliminate any significant fuel pressure fluctuations at the input to the turbine.

- Fuel Flow Meter - Brodie Metering Co.; Positive Displacement flow meter that meters the liquid fuel entering the turbine, this meter provides feedback and totalizing to the turbine control system

- Flow Stop Valve  (secondary protection) CR-Tec; Provides secondary protection for the turbine and is controlled directly by the turbine control system

- Pressure Control Valve – Fischer; Provides pressure control at the turbine generator to maintain a constant pressure flow

Implementation of the Dual Fuel Modification on Turbine Generator

The implementation of the dual fuel modification will occur in Margarita Island, Venezuela and will occur concurrently with the installation of the units.

The implementation of the dual fuel modification package will be directed and overseen by Mechanical and Controls Technical Advisors that have previously installed this modification on other units. The Technical Advisors will collect data and monitor the work of the craftsmen to ensure the systems are installed and commissioned properly. A turn over package will be issued to the Customer for the dual fuel modification scope of work.

The Technical Advisors will make any mark-ups to the original drawings to reflect any deviations required during the implementation works. A final set of drawings will be issued to the customer to reflect the installed systems.

The Controls Technical Advisor will work with the Customer or Installation contractor to modify, adjust, or develop any interfaces for the dual fuel systems.

Below is an outline that describes the sequence of assembly of the dual fuel modification. The outline below is broken out in several sections. The scope of work described in Section 1 - Accessory Skid; and Section 2 - Turbine Skid which can be implemented anytime after the unit is received at the site and can be performed independently of each other.

The scope of work described in item 3 – Interconnection Piping and item 4 – External Scope must be implemented after the accessory and turbine skids are set on the foundation and rough aligned.

- Accessory Skid

  - Install major components – This task should be performed before the skid roof and enclosure is installed so that the equipment can be set with an overhead crane.

    - Atomizing Air Filter

    - Atomizing Air Main Compressor

    - Liquid Fuel Clutch Assembly

    - Install Main Fuel Pump and base

    - Install Main Fuel Stop Valve

    - Install Duplex Fuel Filters, Transfer Valve, and Gauge Panel

    - Install Atomizing Air Booster Compressor Stand, Compressor, and Motor

    - Install Flow Divider / Selector Valve / Isolation Valve Assembly

  - Install large bore piping

    - Liquid Fuel System

      - Fuel filter to main stop valve

      - Main stop valve to main fuel pump

      - Main fuel to bypass and install bypass valve

      - Main fuel pump to flow divider

    - Atomizing Air System

      - Air filter to main compressor

      - Booster compressor to Air Filter and install check valves and isolation valves

  - Install Instrumentation and Conduit

    - Main Stop Valve

    - Liquid Fuel Bypass Valve

    - Flow divider and Isolation Valve

    - Atomizing Air Booster Compressor Solenoid Valve Panel

    - Atomizing Air Booster Compressor Motor

  - Install  tubing

    - Liquid fuel pressure switches

    - Hydraulic & trip oil connections to Liquid Fuel and Stop Valves

    - Instrument air to atomizing air isolation valves

    - Fuel tubing from the flow divider to bulk head fittings at base of accessory module

    - Lube oil feed line to main atomizing air compressor

    - Liquid Fuel Gauge Panel

    - Atomizing Air connections to the gauge panel

  - Pull Cable and Loop check

- Turbine Skid

  - Install liquid fuel tubing along the floor of the skid – ML 961.

  - Install Atomizing Air Heat Exchanger

  - Install lower Atomizing Air Piping (supply and return) and tie into Atomizing Air Heat Exchanger. Install all low point drains on piping.

  - Install Primary Fuel Nozzles

  - Install Secondary Fuel Nozzles

  - Install Atomizing Air and Water Injection headers and tie into supply lines

  - Install Gas Fuel Headers

  - Install Purge Air Headers and supports

  - Install three way purge valves on combustion cans

  - Install gas fuel and atomizing air flex hoses, and  water injection , purge air, and liquid fuel tubing to each nozzle starting with combustion can #5 and #10 working toward the horizontal joint of the unit

  - Install flame detectors and cooling water tubing to them

- Interconnection Piping

- Install Atomizing air System interconnection piping between the turbine and accessory skid

- Install liquid fuel tubing between the turbine and accessory skid

- Install the interconnection piping from the atomizing air system to the purge air system

- Install interconnection piping from the turbine to gas fuel module for gas fuel and purge air

- External Scope (outside of turbine and accessory module)

- Install purge air heat exchanger

- Install piping and valves for the purge air system (under the turbine walkway)

- Tie in cooling water to the atomizing air and purge air heat exchanger

- Install the purge air solenoid valve panel

- Install Purge Air Protection Panel on turbine compartment roof

- Install Tubing

    - Purge air solenoid panel to purge valves

    - Purge Protection Panel to purge headers

- Install Conduit and cable

  - Purge Air Protection Panel to Local JB

  - Purge Air Solenoid Valve Panel to Local JB

  - Loop check

- Skids

  - Gas Fuel Module (Install Modification Kit)

    - Large bore piping, purge and vent valves

    - Pressure switches, tubing, and conduit

    - Insulation on gas fuel piping

  - Water Injection Skids

    - Set skid on foundation

  - Liquid Fuel Forwarding Skids

    - Set skid on foundation

  - Demineralized Water Forwarding Skids

    - Set skid on foundation

Quality Control

A Quality Control person will be on site to oversee implementation of the dual fuel equipment. Weld maps will be made for field welds. All welders performing welds will be tested and certified for welding performed.

The field welds will be inspected according to ASME B31.1 and documented. The Quality Control person will also verify cleanliness of systems, and confirm documentation is provided to confirm proper assembly of the equipment.

Below is the project team to implement the dual fuel modification.

Project Manager

Tom Koontz

Site Manager / Technical Specialist

Daniel Maxey

Engineering & Coordination

Chris Brown

Shop Fabrication

Jeff Pope

Jimmie Ballew

Mechanical Supervisor

Mark Welty

Drafting & Design

Steven Boerckel

Purchasing & Procurement

Jenny Dias

Mechanics (2)

Welders (3)

Fitters (3)

Tool Room (1)

Electrical and Instrumentation Supervisor

Patrick Doran

Electricians (2)

Safety Representative

TBD

Quality Control

As Required - TBD

Note:  positions highlighted in blue are based at headquarters; positions in yellow will be located at the site.

Organizational Structure:  Project Team for the Dual Fuel Modification Project