Section 2.0	Scope of Work and Equipment List

  - The Scope of Work for the proposed project is generally outlined as follows:

- Major Equipment – Owner will supply Two (2) GE Model 7121 Frame 7EA Gas Turbine Generators with auxiliaries and One (1) 13.8KV to 230KV Generator Step Up Transformer (GSU) and a 230 KV substation / switchyard.

    - Contractor will transport from the US to the Port of Maracaibo, Venezuela.  A more detailed description of the Frame 7EA scope is attached.

    - Contractor will provide the Balance of Plant which includes the following outlined list of major equipment and deliver them to site:

- One (1) Oily Water Separator with Waste Oil and Waste Water Tank

- Diesel Fuel Forwarding Pumps and Filtration

- Modular Climatized Control Building

- Instrument/Service Air Compressor

The contractor will design and install the facility as described in the following sections of this document.  The design will include the necessary Civil, Foundations, Structural, Mechanical, Electrical, Instrumentation, and Control System to install the above listed equipment.

    - Balance of Plant – The contractor proposes to furnish and install the Balance of Plant equipment and materials, which comprises the following:

- Complete design of the facility including civil, foundations, structural, buildings, mechanical, electrical, instrumentation and control.

- Contractor will provide design and oversight for the Civil works but Owner will provide the material and labor for the Civil Works

- Owner will provide site preparation and civil work.

- Owner will provide concrete foundations, plant gravel, and fencing if required.

- Owner will provide roads and removal pads as shown.

- Contractor will provide Installation of the complete Power Plant with the inter-ties as described later in this document.

- Contractor will provide mechanical installation of the various items of equipment with the associated inter-ties of treated water, natural gas, liquid fuel, waste water, and Fire Water.

- Contractor will provide installation of the plant including the 230 KV high voltage GSU, 230KV SF6 breaker, 230KV disconnect, dead end tower, grounding, lightning protection, and cathodic protection.

- Contractor will provide Instrumentation and Control Systems including plant instrumentation, metering, and Plant DCS.

- Contractor will install Owner supplied buildings including:

  - GTG PEECC Buildings

  - PDC Building

- Contractor will furnish and install following Buildings:

  - Modular Climatized Control Building

  - Substation Building

- Contractor will also supply the following:

  - Natural Gas Interconnect Piping to Existing Header System Adjacent to Plant

  - Liquid Fuel Interconnect Piping to Owner furnished Day Tank adjacent to Plant

  - Treated Water Interconnect Piping to Existing Header System

  - Treated Water Day Storage

  - Waste Water Interconnect Piping to Existing Header System

  - Fire Water Interconnect Piping to Existing Header System

  - Plant fire Water Underground Piping System with Monitors, Hydrants, Etc.

- Project Management, QA/QC, Safety and Training.

- In addition, the Contractor will perform:

- Plant commissioning, check out, start up, and training with Vendor Technical Representatives present.

- Plant Performance, Reliability, and Environmental Testing.

- Furnishing of plant documentation including Vendor Information, Warranty, Engineering, Turnover documents, O&M Manuals and As Built Drawings.

2.2	Equipment List - Detailed Division of Responsibility

| Material/Responsibility | Qty | Description |
| --- | --- | --- |
| OWNER | 2 | GE Model 7121 Frame 7EA (60Hz) Gas Turbine Generators with Associated Equipment as Coming From Southhaven Including: |
|  |  | 1 Electrical PDC Building |
|  |  | 2 13.8 KV 5000 amp Gas Turbine Generator Breaker NEMA 3R |
|  |  | 1 230 KV SF6 Circuit Breaker |
|  |  | 1 230 KV Disconnect Switch |
|  |  | 1 13.8 KV / 480 V 3000 KVA Station Service Transformer |
|  |  | 1 13.8 KV / 4160 V 3380 KVA Station Service Transformer |
|  |  | 2 480 V GTG MCC |
|  |  | 1 480 V Distribution board |
|  |  | 2 230KV Dead End Towers |
|  |  | 1 Lot 230 KV Insulators and ACSR Cable Bus & Fittings |
|  | 1 | 13.8 KV / 230 KV Generator Step up transformer (2 ea. GTG capacity) |
|  | 1 Lot | Project Site free and clear of rock and ground water |
|  | 1 Lot | Removal of all unused building foundations, underground piping, etc. on the proposed project site |
|  | 1 Lot | Site Preparation, Rough Grading, Excavation, and final grading |
|  | 1 Lot | Plant Concrete Foundations |
|  | 1 Lot | Plant Paving, Gravel and Pads for Turbine and Generator removal. |
|  | 1 Lot | Local Subcontractor(s) Civil Material and Craft Labor |
|  | 1 Lot | Natural Gas Fuel Tie in Point at Plant Boundary with measurement |
|  | 1 Lot | #2 Diesel Fuel Supply and Day Tank adjacent to Plant |
|  | 1 Lot | Treated Water Supply to Inter-tie Point |
|  | 1 Lot | Treated Water for Commissioning and Startup |
|  | 1 Lot | Waste Water Disposal Line at Inter-tie Point |
|  | 1 Lot | Eight (8) Telephone Circuits to Project Site |
|  | 1 Lot | Permits for Environmental, Transportation, Building, Construction, Operations, etc. |
|  | 1 Lot | Construction & Commissioning Water and 480V three phase power |
|  | 1 Lot | Access Roads to site |
|  | 1 Lot | Import Duties and Taxes |
|  | I Lot | Construction lay down area (3 acres) adjacent to project site |
|  | I Lot | Architectural Treatment and landscaping |
| CONTRACTOR |  |  |
| Buildings |  |  |
|  | 1 | Modular Climatized Control Building |
|  | 1 | Substation Building |
| Mechanical |  |  |
|  | 2 | 100% Treated Water Forwarding Pumps |
|  | 6 | Demineralized Gallon Water Storage Tanks, 21,000 Gallon each |
|  | 2 | 100% Demineralized Water Forwarding Pumps for Turbine Wash |
|  | 1 | Oily Water Separator |
|  | 1 | Waste Oil Tank, 10,000 Gallon. |
|  | 1 | Waste Oil Delivery Pump |
|  | 1 | Waste Water Tank, 10,000 Gallon |
|  | 1 | Waste Water Delivery Pump |
|  | 1 | Instrument Air Package with two compressors, receiver, filters and dryer |
| Contractor (cont’d) |  |  |
| Mechanical |  |  |
|  | 2 | Liquid Fuel forwarding Pumps |
|  | 4 | Liquid Fuel Filters |
| Electrical |  |  |
|  | 1 | 480 V BOP MCC |
|  | 1 | 480 V Distribution Board |
|  | 1 Lot | BOP 480 V / 120 V Transformers, Lights, Panels etc. |
|  | 1 | UPS System for Control Room |
|  | 4 | Welding Receptacles |
|  | 1 | Plant Grounding Grid |
|  | 1 Lot | Lightning Protection |
|  | 1 Lot | Cathodic Protection for underground steel piping |
|  | 1 Lot | Area Lighting |
| I&C |  |  |
|  | 1 Lot | Plant Instrumentation |
|  | 1 | Plant DCS System |
| Construction |  |  |
|  | 1 Lot | Construction Tools, Rental Equipment & Rental Cranes |
|  | 1 Lot | Temporary Power Distribution |
|  | 1 Lot | Local Subcontractor(s) Electrical & Mechanical Craft Labor |
|  | 1 Lot | Transportation of all Contractor supplied BOP equipment |
|  | 1 Lot | Construction Offices, Storage, Temporary Facilities and Utilities |
|  | 1 Lot | Lubricants, Chemicals, Filters, etc. for Plant Commissioning |
|  | 1 Lot | Balance of Plant Start up and Commissioning Spare Parts |
| Engineering |  |  |
|  | 1 Lot | Conceptual and Detail Design Engineering (Total Plant) |
| Project Management |  |  |
|  | 1 Lot | Project Management with QA/QC, safety, and training |
|  | 1 Lot | Plant Commissioning and Testing |
|  | 1 Lot | Overall Plant Training |