Section 4.0	Design Basis and Interconnect Points

4.1	Design Basis

| Design Conditions |  |
| --- | --- |
| Site Elevation | 100 ft. |
| Air Temperature, High | 104ºF |
| Air Temperature, Low | 60ºF |
| Design Temperature | 85ºF |
| Relative Humidity | 60% |
| Wind Speed | 80 mph |
| Gas Turbine Power | 75 MW net |
| GTG Fuel Consumption Rate | 42,000 MCFD Natural Gas |
| GTG Liquid Fuel Consumption Rate | 260 gpm |
| High Voltage Interconnect | 230 KV |
| Demin Water Storage | 126,000 Gallon (6) Fiberglass Tanks by Contractor |
| Instrument Air System | 85 SCFM by Contractor |
| Waste Oil Storage | 10,000 Gallons by Contractor |
| Waste Water Storage | 10,000 Gallons by Contractor |
| Raw Water Storage | 2,000,000 Gallon CS Tank by Contractor |
| Treated Fuel Storage | 125,000 Gallon Storage Day Tank by Owner |

  - Interconnect Points

| Natural Gas at min. 450 psig | Owner to provide interconnection point outside of the Plant Battery Limits. |
| --- | --- |
| Treated Liquid Fuel | Owner to provide pipeline and measurement at Plant Battery limits |
| Plant Waste Water | Plant Battery Limits. |
| Plant Waste Oil | Plant Waste Oil Tank. |
| 230 KV | Connection to Utility via dead end structure inside Substation. |
| Telephone | Plant Battery Limits. |
| Raw Water Supply | Plant Battery Limits. |
| Sanitary Sewer | Existing Plant Septic System at boundary |
| Raw/Firewater Supply | Plant Battery Limits by Owner |