Section 4.0	Design Basis and Interconnect Points

4.1	Design Basis

| Design Conditions |  |
| --- | --- |
| Site Elevation | 50 ft. |
| Air Temperature, High | 104ºF |
| Air Temperature, Low | 60ºF |
| Design Temperature | 85ºF |
| Relative Humidity | 60% |
| Wind Speed | 8 mph |
| Gas Turbine Power | 75 MW net each Gas Turbine |
| High Voltage Interconnect | 230 KV |
| Natural Gas Usage | 21.2mm SCFD per Turbine 42.4mm SCFD Total |
| Liquid Fuel Usage | 126 GPM per Turbine – 252 Total |
| Liquid Fuel Storage | 120,000 Gal – 8 hr Supply – By Owner |
| Treated Water Injection | 111 GPM per Turbine – 222 Total when on Diesel Fuel |
| Inlet Air Fogging | 25 GPM per Turbine – 50 Total |
| Treated Water Usage | 272 GPM Total |
| Treated Water Storage | 125,000 Fiberglass Tanks by Contractor, 8 hr supply |
| Firewater System | Fire Water Supply by Owner |
| Waste Oil Storage | 10,000 Gallons by Contractor |
| Waste Water Storage | 10,000 Gallons by Contractor |
| Instrument/Service Air System | 85 SCFM by Contractor |

  - Interconnect Points

| Natural Gas at min. 450 psig | Pipeline Header System Adjacent to Plant |
| --- | --- |
| Liquid Fuel Storage | Owner Furnished 120,000 Gal Tank Located Adjacent to Plant |
| Treated Water Supply | Pipeline Header System Adjacent to Plant |
| Plant Waste Water | Pipeline Header System Adjacent to Plant |
| Plant Waste Oil | Plant Waste Oil Tank. |
| Fire Water Supply | Pipeline Header System Adjacent to Plant |
| 230 KV | Connection to Utility via dead end structure at Substation battery limits. |
| Telephone | Plant Battery Limits. |