## Slide 1
1st Stage Blade trailing edge.
1st Stage Vanes, outer bushing. Wear on bushing.
Minor Rotor to Case Rubs on 2nd Stage.
Oil Sheen throughout Compressor.

## Slide 2
Minor Rotor to Case rubs, 4th & 5th Stage.

## Slide 3
Minor Metal Splatter 14th Stage with no apparent Leading edge damage. Appears to be in good shape.

## Slide 4
Minor burns on Dome Plate assy’s.

## Slide 5
1st Stage Nozzles have some clogged cooling holes and also a blue-green mildew is present in the 1st stage shrouds.
Radial Cracking on all 1st stage blades viewed.
Gouging on 1st Stage shrouds and mildew.

## Slide 6
1st Stage Shroud Gouging and 1st Stage blade damage from impacting shroud.
Burn through on convex side of 1st Stage Nozzle Platform. TBC loss on Convex Surface of 1st Stage Nozzle.

## Slide 7
Damage on Convex side of all 1st Stage Blades.
2nd Stage Blades appear to be serviceable.