| CLIENT: | BIE REF. / REPORT No.: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Bariven S.A. c/o PDVSA Services BV President Kennedylaan 19 2517 JK The Hague The Netherlands | I-BA-003/10_22 |  |  |  |  |  |  |  |  |  |  | PAGE 1 OF 14 |  |  |  |  |  |  |
|  | CLIENT P.O. No.: |  |  |  | VISIT No.: |  |  |  |  |  |  | NEXT SCHED. VISIT: |  |  |  |  |  |  |
|  | 5100077213 |  |  |  | 4519C.04 |  |  |  |  |  |  | None |  |  |  |  |  |  |
| VENDOR: | W.O. / REQ No.: |  |  |  | INSPECTOR: |  |  |  |  |  |  | BASE: |  |  |  |  |  |  |
| Derwick Associates MMG Tower Piso 16 Calle 53, Urb, Panama | 2232 |  |  |  | Bill Skoug |  |  |  |  |  |  | Huntington Beach, California |  |  |  |  |  |  |
|  | VENDOR REF. No.: |  |  |  | INSPECTION DATE(S): |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 03 February 2010 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUB-VENDORS: |  | LOCATION: |  |  |  |  |  |  |  |  | SUB-VENDOR REF. No.: |  |  |  |  |  |  |  |
| Wood Group Pratt & Whitney |  | Santa Fe Springs, California |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |
| CLIENT P.O. BRIEF MATERIAL DESCRIPTION: |  |  | I-1 | 3.0 |  | Hrs |  | I-3 | 2 | Hrs |  |  |  | I-4 | 74 KMS |  | I-5 | $0 |
| Turbo Generator Sets |  |  | INSPECTION AT: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Sub-Vendor (Wood Group) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUB-ORDER – BRIEF MATERIAL DESCRIPTION: |  |  | ORDER STATUS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| USED – 6300 KVA Generator |  |  | In Process |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| P.O. ITEM | P.O. QTY. | QTY ACC. | QTY REJ. | NARRATIVE | QP STAGE |
| --- | --- | --- | --- | --- | --- |
| 4 | 1 | 0 | 0 | 1-62500 KVA, 3000A, 12000V, 60HZ Electric Generator with Brushless Excitation EM Serial Number 173228201 |  |

INSPECTION VISIT OF 03 FEBRUARY 2010: SUMMARY: An inspection visit was made to the Wood Group facilities in Santa Fe Springs, California to inspect one (1) each used 6300 KVA Generator that was manufactured by the Electric Machinery Manufacturing Company (EM) located in Minneapolis, Minnesota. EM is a division of the Turbodyne Corporation. BIE recommend PI (Polarization Index Testing) before acceptance. Personnel in attendance: Omar Petit - Proenergy Mike Fieldhouse - Wood Group Field Services Inc. William Skoug - BIE inspector representing PDVSA VISUAL AND DIMENSIONAL INSPECTION: Initial inspection of the generator nameplates revealed the following:

MAIN NAMEPLATE –	(note – no manufacturing date was found on the generator)

Serial Number:	771195701

KVA:	6300

Volts:	13800

Amps:	2640

Rpm	3600

Hertz	60

P.F.	90

3 Phase

SECONDARY NAMEPLATE

Machine Serial Number:	771195701

Rotor Production Serial Number:	771195701

Stator Production Serial Number:	771195701

Assembly and Test Serial Number:	771195701

SECONDARY NAMEPLATE - #2

- Phase sequence:	1-2-3

- Rotation:	CCW facing Exc. end

- Inlet air temperature:	59 F° at 0’ altitude

The overall appearance of the generator indicated the following:

- paint rusting and peeling off

- no structural damage apparent

- generator shaft at both ends in good shape – no damage noted

- junction box missing cover

- conduit runs missing brackets

- minor bolting missing on covers

- suspect conduit wiring broken in various locations

- flanged connections covered with wood to protect

Mr. Fieldhouse advised that Leppert Nutmeg examined the generator externally and internally and advised that the generator was in serviceable condition.  Mr. Fieldhouse was to forward the Leppert Nutmeg report to Mr. Petit who in turn would forward it provide it to B.I.E.

INSPECTION RELEASE:

Not issued.

ATTACHMENTS:

Digital Photographs (imbedded)

GENERATOR IN REPOSE

COUPLING END

COUPLING END

PAINT CONDITION

MANUFACTURERS NAMEPLATE

NAMEPLATE – LUBRICATION

NAMEPLATE

GENERATOR MAIN NAMEPLATE – MANUFACTURE DATE MAY HAVE BEEN AT BOTTOM OF NAMEPLATE HOWEVER IT IS SO WORN AS TO BE ILLEGIBLE

COUPLING END

JUNCTION BOX

GENERATOR SIDE VIEW

JUNCTION BOX – NO COVER

- END OF REPORT -