Section 2.0	Scope of Work and Supply (Preliminary)

The Scope of Work and Supply is comprised of the following outlined items:

Major Generation Equipment

Installation of one (1) Owner Supplied GE LM2500 PE gas turbine generator package complete with auxiliary skids, inlet filter and exhaust stack adjacent to Owner’s existing LM 2500 Package.

GE LM 2500 GTG interface points are as follows:

| Equipment System | Limits of GE Aero Energy Scope |
| --- | --- |
| - All supply piping, including Fuel Gas, Steam, Cooling Water, Heating Water, Demineralized Water, Lube Oil, Compressed Air, Instrument Air, Hydraulic Start Oil | - Flanged or threaded connection on GE Aero Energy base plates. |
| - Inlet Air-to-Filter | - Atmosphere (non-standard duct by others) |
| - Turbine/Generator Ventilation Air | - Atmosphere (non-standard duct by others) |
| - Turbine Exhaust | - Flange & Expansion Joint for connection to Exhaust Stack or SCR |
| - Instruments on GE Aero Energy Base plate | - Terminal box on base plate |
| - Instrument wiring in Turbine Control Panel | - Terminal in Turbine Control Panel |
| - High Voltage Connections | - Bus bar in GE Aero Energy generator line side cubicle |
| - Generator Ground Connections | - GE Aero Energy Neutral cubicle |
| - Electric Motors | - Terminal box on individual motors |
| - Ladders and Platforms for Air Filter | - Ladders and Platforms for Inlet Air Filter and Vent Fans |

.

  - Balance of Plant

The contractor will design and install the facility as described in the following sections of this document.  The design will include the necessary Structural, Mechanical, Electrical, Instrumentation, and Control System to install the above Major Equipment.

The Balance of Plant scope of supply will be comprised of the following:

- Contractor will provide complete design of the facility including civil, structural, modular building, mechanical, electrical, instrumentation and control.

- Contractor will provide concrete foundations.

- Owner will provide a reasonably level graded site.

- Owner will provide access roads to the site.

- Contractor will provide Installation of the complete Power Plant with the inter-ties as described later in this document and including:

- Mechanical installation of the various items of equipment with the associated inter-ties of liquid fuel, and fuel gas.

- Electrical installation of the plant including a new 13.8 KV interconnect to Owner’s existing substation with one (1) open bay for connection to Owner provide GSU, grounding, lightning protection, and cathodic protection.

- Installation of Instrumentation and Control System including plant instrumentation, metering.

  - BOP Major Mechanical Systems

    - Simple Cycle Exhaust Stack

The Contractor will install a 40ft. exhaust stack in accordance with the standards set out by GE for each LM2500 machine.

    - Plant Fuel Gas System

The Contractor will install the plant fuel gas system outlined as follows:

- Interconnect to Owner gas metering station above ground at the Fuel Gas Supply Station.

- Connect at this 500 psig source and run pipeline to existing LM 2500 GTG site.

- Install two (2) redundant coalescing filter separators on a common skid including redundant pressure regulators.

- Install all plant fuel gas carbon steel piping, valves and fittings from plant inlet fuel gas interconnect to the new fuel gas regulator filter skid at the new LM 2500 site

- Install stainless steel piping from the fuel gas filter to the gas turbine generator.

    - Plant Liquid Fuel System

The Contractor will design and install the plant liquid fuel system outlined as follows:

- Install one (2) Duplex liquid fuel filter/regulator skids.

- Install one (1) 100% capacity liquid fuel injections pump skids.

- Provide and install all plant liquid fuel carbon steel piping, valves and fittings from the plant liquid fuel pipeline to liquid fuel filter regulator skids

- Provide and install all plant liquid fuel stainless steel piping, valves and fittings from the plant liquid fuel filter regulator skids to the liquid fuel injection pumps and on to the gas turbine

    - Water System (Not Required)

    - Oily Water Drain System

The Contractor will utilize Owners existing the oily water drain system as follows:

- Furnish and install PVC or HDPE below ground piping and fittings from concrete waste oil/water containments located at:

- Gas Turbine Generator Auxiliary Skids

Piping is to be routed to the existing oily water separator.

    - Plant Fire Water Header System:  (Not Required)

    - Instrument and Service Air Systems

The instrument and service air systems will be as follows:

- Furnish and install one (1) set of instrument and service air screw compressors with associated dryer and air storage tanks.

- Furnish and install carbon steel piping, valves, fittings and instruments for instrument and service air systems from the air compressors to various required areas throughout plant for instrument air and service air.  Furnish the appropriate quick connect connectors.

  - BOP Electrical Systems

    - 13.8 KV System

The Contractor will perform the following work on the 13.8 KV system:

- Furnish and install one (1) each 13.8 KV 2,000 amp generator vacuum circuit breaker with PTs and CTs.

- Furnish and install all 13.8 KV cabling, bus work, cable tray etc. from the generator to the generator circuit breaker.

- Furnish and install a 13.8KV cable underground and in overhead cable tray from Generator Breaker to Owner’s substation.  Owner to connect to their GSU.

    - 13.8/4.16 KV System  (IF REQUIRED)

The Contractor to provide the following:

- Furnish and install one (1) 13.8 KV fused switchboard .

- Furnish and install one (1) 13.8KV / 480 volt auxiliary power transformer.

    - 480V System

The Contractor will provide the 480V system as follows:

- Furnish and install one (1) 480 V distribution switchboard

- Furnish and install one (1) gas turbine generator MCC.

- Furnish and install one (1) BOP 480V MCC

- Furnish and install cable tray / conduit with cabling from transformers to MCCs and from MCCs to plant 480V equipment and motors.

- Furnish and install underground conduit, duct banks, or overhead cable tray mounted on the pipe racks.

    - 120/208 System

The Contractor will provide the 120/208 system as follows:

- Furnish and install 480V/120/208V transformers, distribution panels and lighting panels as required with associated conduits, fittings and wire.

    - Plant Area Lighting (Not Requred)

    - Ground Grid

The Contractor will provide the ground grid for the plant as follows:

- Furnish and install plant ground grid with associated ground rods and connections to plant equipment, buildings and fence.

    - Plant Electrical Cable Tray

The Contractor will provide the plant electrical cable tray work as follows:

- Furnish and install aluminum cable trays throughout plant.  Cable trays to be mounted on pipe racks, cable trenches or within buildings for routing plant cabling.  A separate cable tray will be installed for each of the 15/5KV systems, 480V system, and instrumentation system cables.

    - Underground Conduit and Cable Systems

The Contractor will provide the plant underground conduit and cable system as follows:

- Furnish and install rigid galvanized conduit or PVC encased in concrete for all underground power, control and instrumentation systems.

    - Lightning Protection

The Contractor will provide lightning protection as follows:

- Furnish and install lightning protection on each gas turbine exhaust stack.

    - Batteries / Chargers / UPS Systems

The Contractor will perform the following work on the batteries / chargers / UPS systems:

- Furnish and install BOP UPS system for DCS and associated equipment.

- Furnish and install one (1) 125V DC battery and charger for 13.8KV plant switchgear.

Note:  24 VDC and 125VDC batteries and chargers are to be supplied as part of the GE packaged control house.

  - Plant Instrument and Control Systems

    - BOP Control System (Not Required)

    - Plant Instrumentation Devices

- Gas Turbine Control Panel is supplied with each LM2500 gas turbine. The Control Panel will be mounted in a new modular Control Building.

- Contractor to furnish and install instrument devices, both pneumatic and electric, consisting of meters, pressure, flow, temperature and level where required.

    - Electronic Wiring and Pneumatic Piping

- Contractor to furnish and install necessary instrument wiring and pneumatic piping with associated Swagelok fittings, etc.

  - 13.8 KV  to Owner’s Substation

    - Generator Step-up Transformers (GSU) – BY OWNER

- Owner to supply and install one (1) generator step-up transformer with 13.8KV delta to 34 KV wye windings

- Contractor to provide underground cable and overhead tray from LM 2500 Generator Breaker  to Owner’s substation.  Owner will connect 13.8 KV cable to their substation GSU, etc.

  - Plant Communication System

- Not Required.

  - Plant Civil and Structural

- Site preparation, rough grading, and finished grading to be furnished by Contractor based on an existing site requiring minimal cut and fill.

- Contractor to furnish and install all plant reinforced concrete foundations designed to IBC 2003.  GSU foundation shall have 9” freeboard.

- Contractor to furnish and install concrete containment curbs and equipment foundations, including ammonia truck filling area.

- Contractor to furnish and install plant gravel and asphalt paving as shown on the Plot Plans.

- Contractor to provide structural steel pipe racks to support overhead piping and cable trays. Pipe racks to be located as shown on Plot Plan drawings.

  - Plant Building

- Furnish and install a (11ft. x 40ft.) prefabricated metal insulated building for the Control / PLC room and MCC’s.   The Control / PLC room will be air conditioned and finished out as office space.

  - Plant Equipment Erection

- Contractor to unload all Plant equipment delivered to site.

- Contractor will provide all cranes and support equipment and manpower as required to erect the gas turbine generator.

- Contractor to provide for erection of all BOP equipment.

  - Cranes, Equipment and Tools

Contractor to furnish or provide for all plant construction required cranes, fork lifts, back hoes, hydraulic lifts, welding machines, air compressors, generators, temporary lights, trucks, pick-ups, etc.

  - Transportation

Contractor will furnish transportation to site of all furnished equipment.

.

  - Lubricants and Chemicals

- Contractor will supply and install all lubricants, lube oils and chemicals for furnished equipment. .

  - Spares

- Contractor will make provision to supply, receive and store all commissioning spare parts furnished for equipment during start-up and commissioning.

- Contractor to provide Owner with recommended list of spare parts for Gas Turbine Generator and BOP equipment.

  - Construction Offices and Storage Facilities

- Contractor to provide construction offices for Contractor, Technical Representatives (2), and Owner.

- Owner to provide one (1) acre lay down area and site for construction offices and construction utilities (electrical and potable water)

- Contractor to provide fenced storage and a lay down area and around the construction site during construction.

- Contractor to provide sanitation facilities for Contractor and Owner personnel during construction.

- Contractor to provide communication facilities for construction.

  - Engineering and Project Management

- Contractor to provide detailed engineering and specifications for all disciplines involved for the power plant including civil and concrete foundations.

- Contractor to provide project management complete with construction management, quality control / quality assurance, scheduling, administration, warehousing, and expediting including regular monthly reporting of all disciplines.

- Contractor to arrange for and provide fully qualified technical representatives during erection, testing, start-up, commissioning for the gas turbine generator units and Chillers.

- Contractor to provide startup, commissioning and testing of BOP associated systems.

- Contractor to provide operator and maintenance training for Power Plant on the Gas Turbine Generator Packages, Chillers, DCS, and Balance of Plant.

- Contractor to provide one (1) electronic and two (2) hard copies of the O&M manuals, training manuals, engineering calculations, commissioning and start-up manuals, test manuals, as-built drawings, design specifications and warranty manuals for plant equipment.

  - Cathodic Protection

Cathodic Protection will be provided for all steel underground piping.

  - Project Equipment List and Supplier

|  |  | Responsibility |  |
| --- | --- | --- | --- |
| Qty | Description | Owner | Contractor |
| 1 | Power Plant Site with survey | xxx |  |
| 1 lot | Site permits if required (Environmental, etc.) | xxx |  |
| 1 | Construction permit (if required) | xxx |  |
| 1 lot | Import duties, sales taxes, VAT, etc. (if required) | xxx |  |
| 1 | GE LM2500 PE Gas Turbine Generator Package | xxx |  |
| 1 | GTG Turbine Control Panels to be located in the new, prepackaged control house | xxx |  |
| 1 | Set of GTG batteries and chargers each set consisting of 2ea 24 volt batteries and 2ea chargers to be located in the Battery Room | xxx |  |
| 1 lot | Oil disposal during operations | xxx |  |
| 1 | GE LM2500 PE Gas Turbine Generator Package equipped with a prepackaged, modular control house. |  | xxx |
| 1 | Soil test report |  | xxx |
| 1 lot | Water supply to site for construction and operations |  | xxx |
| 1 lot | Construction Power |  | xxx |
| 1 lot | Oil disposal during Construction |  | xxx |
| 1 lot | Site Preparation and grading |  | xxx |
| 1 lot | Concrete Foundations |  | xxx |
| 1 lot | Site Gravel and Paving |  | xxx |
| 1 lot | Plant construction and lay down area temporary fencing and gates |  | xxx |
| 1 lot | Plant security during construction |  | xxx |
| 1 | Exhaust Stack |  | xxx |
| 1 | Prefabricated insulated metal building with air conditioned Control and Electrical Rooms. |  | xxx |
| 1 | Gas ESD Block Valve |  | xxx |
| 1 | Duplex Fuel Gas Regulator Coalescing Filter Skids |  | xxx |
| 1 | Duplex Instrument / service air compressor with dryer and dual storage tanks |  | xxx |
| 1 | 13.8KV Generator Circuit Breaker 2000 Amp NEMA 3R |  | xxx |
| 1 | 13.8 KV Fused Switch NEMA 3R |  | xxx |
| 1 | 13.8KV to 480V Transformers |  | xxx |
| 1 | 480V MCC for Gas Turbine Generator |  | xxx |
| 1 | 480V MCC for Balance of Plant |  | xxx |
| 1 | 480V Switchboard |  | xxx |
| 1 lot | Balance of plant (BOP) 480V/120/208V Transformer, Distribution Panels, Lighting Panels |  | xxx |
| 1 | Plant Ground Grid |  | xxx |
| 1 Lot | Plant Instrumentation |  | xxx |
| 1 | Power Plant PLC System, if required |  | xxx |
| 1 | Lot fencing for construction and storage |  | xxx |
| 1 lot | Start up and commissioning spare parts |  | xxx |
| 1 lot | Plant Cathodic Protection of Buried Piping |  | xxx |
| 1 lot | BOP Equipment Erection |  | xxx |
| 1 lot | Transportation of all Contractor Furnished Equipment |  | xxx |
| 1 lot | Lubricants and Chemicals for gas turbine generator |  | xxx |
| 1 lot | Lubricants and Chemical for BOP |  | xxx |
| 1 lot | Construction Offices, Storage, Temporary Facilities and Utilities |  | xxx |
| 1 lot | Construction Tools and Equipment |  | xxx |
| 1 lot | Temporary Power Supply (500KVA) |  | xxx |
| 1 lot | Temporary Power Distribution |  | xxx |
| 1 lot | Engineering and Project Management, Safety, QA/QC, subcontracting for civil, mechanical, electrical & instrumentation. |  | xxx |

1-1

______________________________________________________________________________

Section 1.0 Introduction