## Proposal_Notes ^^^
FT-8 MobilePac (Liquid Fuel - WI / DRY)
Sheet-1, Notes Applicable to Performance and Emissions Data
Standard Mobile Pac - 60Hz, 13.8kV, 0.9Pf (Liquid Fuel)
PerfCustCpy_Standard-MP_LF_60Hz_13.8kV_0.9Pf_MJ_R0-111308.xls
Notes:
0. All Performance/Emissions Data submitted are subject to the sum of the following notes.
1. The MobilePac(MP) consists of one turbine driving a generator. Rates are shown as per MP.
2. Liquid fuel supplied to gas turbines must meet PWPS fuel specification FR-1.
3. Water used for burner injection must meet PWPS specification AR-1 (demin water).
4. Performance and emission data shown for both WI and DRY (without WI) cases.
5. Water injected data is shown for 42 ppmvd for liquid @15% O2.
6. All data supplied based on sea level altitude (101.33 kPa) and 60% relative humidity.
7. Site performance to be corrected for changes in ambient temperature, ambient pressure, and relative humidity.
8. Inlet loss estimated at 63.5 mm W.C., w/2-stage inlet filter.
No correction of test results for inlet loss.
9. Exhaust loss for all cases estimated at 25.4 mm W.C. for std. exhaust stack.
There will be no correction of test results for exhaust loss in simple-cycle.
10. Secondary cooling air is mixed with Primary exhaust flow, and exhaust at stack. All emission concentrations corrected to 15% O2.
11. Data designated as "primary exhaust" is referenced to the GT exhaust and does not include secondary cooling air.
12. Data designated as "stack exhaust" includes secondary cooling air flows.
13. All data submitted is based upon DBAX 62-170 generator, 60Hz PT operating at 60Hz, 13.8kV, and 0.9 Pf, per specification.
14. Net Power = Power measured at the generator terminals, minus auxiliary loads for power island.
15. GSU losses, BOP and gas compression loads are not included in Net Power output or Net Heat Rate determinations.
16. Guaranteed values indicated by the following designations, all other data are estimates: (G) or |  | value
17. Performance Acceptance Test for GT Net Power Output and GT Net Heat Rates to be conducted per PWPS test procedures,
instrumentation, and calculations; all being in accordance with ASME PTC-22 and PTC-19.1, which shall meet or exceed
the requirements of ISO 2314, ISO 5167, and ISO 6976.
18. Performance acceptance testing for GT Net Power Output and GT Net Heat Rate shall be furnished by PWPS through independent
third party contractor.
19. Test boundary shall be Ambient Temperature as defined by the average dry bulb temperature at the inlet filter face.
20. Performance and emissions are based upon assumed fuel compositions shown on sheet - 2.
21. SO2 data is estimated from Sulfur contents stated on sheet - 2, which PWPS does not control and therefore can't guarantee.
22. All emission measurements to be by US EPA methods. All emissions testing and procedures to be furnished by Purchaser,
and shall conform to PWPS Quality Assurance procedure: "McHale PWPS EmissionsTuningQAProcedure 0001ETQAR1.pdf"
23. Volatile Organic Compounds (VOC) are defined as non methane, non ethane, > 85% of the composition
being ethene. Values shown are based upon PWPS experience and measurement using EPA Method 25.3.
24. Emission data is representative of steady-state operation, and may not be indicative of transient operation.
25. Tested NOx concentrations shall be corrected lower for liquid fuel bound nitrogen (FBN) in excess of 0.015% by weight.
26. While guarantees have been provided for multiple configurations per fuel, PWPS will only test and be required to demonstrate
Guaranteed performance for one configuration per fuel.
27. Demonstration of (G) emission concentrations for NOx, CO and VOC's are based on 1-hour averages, after operation under
steady-state conditions for 2-hours. Compliance with guarantees shall be based on the average of stack traverse's.
28. Design of the CEMs system, ports, port locations, probes, probe lengths, probe types, and how well the CEM system will read the
average of the stack traverse's, is outside of the PWPS scope of supply.
29. Particulate samples shall be drawn isokinetically, with a minimum of 3-hour sample duration and are to consist of 3-tests.
Sheet 1 - of - 6

## Fuel Properties
FT-8 MobilePac (Liquid Fuel - WI / DRY)
Assumed Fuel Properties
Standard Mobile Pac - 60Hz, 13.8kV, 0.9Pf (Liquid Fuel)
The following fuel properties are assumed as representative of site fuels in lieu of specified data.
Standard No.-2 Fuel Oil
|  | Weight % |  | Units
Carbon |  | 87.115 | Hydrogen to Carbon Ratio |  | 0.14698
Hydrogen |  | 12.804 | Higher Heating Value | Btu/lb | 19553
Nitrogen |  | 0.020983 |  | kJ/kg | 45480.278
Oxygen |  | 0.0099919 | Lower Heating Value | Btu/lb | 18360
Sulfur Max |  | 0.04996 |  | kJ/kg | 42705.36
Total |  | 100 | Ratio HHV/LHV |  | 1.065
|  |  | Specific Gravity |  | 0.8159
PerfCustCpy_Standard-MP_LF_60Hz_13.8kV_0.9Pf_MJ_R0-111308.xls
Sheet - 2

## LF_WI_Base-Loads
FT-8 MobilePac (Liquid Fuel - WI / DRY)
Estimated Performance and Emissions, 100% Base-Load Data
Standard Mobile Pac - 60Hz, 13.8kV, 0.9Pf (Liquid Fuel)
Configuration: Liquid Fuel, Sea Level, 60%RH, DBAX 62-170 Generator at 50 Hz, 10.5kV, 0.9Pf, WI-42ppmvd, Simple-Cycle.
Performance Data
Fuel Type |  | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid
Number of GT's in Operation | No. | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Water Injection In-Service | Yes / No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Percent of MobilePac Rating | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Ambient Temperature | Deg F | -4 | 5 | 14 | 23 | 32 | 37.5 | 41 | 50 | 59 | 68 | 77 | 86 | 95 | 104 | 113 | 122
Ambient Pressure | Psia | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696
Relative Humidity | % | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Inlet Loss | Inch H20 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5001 | 2.5 | 2.5
Exhaust Loss | Inch H20 | 1.0003 | 1 | 0.99986 | 1 | 1.0001 | 1 | 1.0003 | 1.0004 | 1.0002 | 0.99968 | 0.99978 | 1.0001 | 0.99968 | 0.99994 | 1.0002 | 0.99973
Fuel LHV | Btu/lb | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360
Ratio of HHV to LHV |  | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065
Gross Power Output | MWe | 28.4767 | 28.5016 | 28.5089 | 28.5416 | 28.5398 | 28.538 | 27.9135 | 26.4787 | 25.3176 | 24.1419 | 23.0382 | 21.99 | 21.0696 | 20.1911 | 19.3065 | 18.5197
Gross Heat Rate, LHV | Btu/kWhr | 9106.0164 | 9149.0152 | 9193.1056 | 9237.8944 | 9286.0178 | 9316.7125 | 9357.8217 | 9471.0494 | 9589.2957 | 9724.7106 | 9866.7208 | 10016.2608 | 10164.3308 | 10319.7765 | 10490.4912 | 10666.2225
Power Isle Aux Loads | kW | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172
Net Power Output | MWe | 28.3047 | 28.3296 | 28.3369 | 28.3696 | 28.3678 | 28.366 | 27.7415 | 26.3067 | 25.1456 | 23.9699 | 22.8662 | 21.818 | 20.8976 | 20.0191 | 19.1345 | 18.3477
Net Heat Rate, LHV | Btu/kWhr | 9161.3512 | 9204.5624 | 9248.9061 | 9293.9022 | 9342.3209 | 9373.2052 | 9415.8411 | 9532.9736 | 9809.3662 | 9794.4919 | 9940.9385 | 10095.223 | 10247.9894 | 10408.4419 | 10584.7902 | 10766.2127
Fuel Flow, per MP | lbs/hr | 14123.6 | 14202.7 | 14274.8 | 14360.8 | 14434.7 | 14481.5 | 14227.1 | 13659.1 | 13223.2 | 12787.2 | 12380.8 | 11996.6 | 11664.4 | 11349 | 11031.3 | 10759
Burner Water Injection Flow, per MP | gal/min | 28.0783 | 28.8348 | 29.5589 | 30.3289 | 31.0632 | 31.5117 | 30.9045 | 29.6243 | 28.7588 | 27.894 | 27.0941 | 26.3365 | 25.7046 | 25.0935 | 24.4487 | 23.9154
Emissions & Exhaust Conditions at Stack Exit, After Addition of Secondary Cooling Air*
NOx | ppmvd | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
NOx, as NO2, per MP | lbs/hr | 49.2127 | 49.4964 | 49.7556 | 50.0633 | 50.3286 | 50.4966 | 49.6079 | 47.6249 | 46.1053 | 44.5857 | 43.1699 | 41.8324 | 40.6769 | 39.5805 | 38.4764 | 37.532
CO | ppmvd | 25.751 | 23.3583 | 21.3828 | 19.7314 | 18.1258 | 17.1377 | 17.2939 | 17.4349 | 17.1845 | 16.9162 | 16.626 | 16.3374 | 15.9952 | 15.6879 | 15.4693 | 15.1987
CO, per MP | lbs/hr | 18.3704 | 16.7595 | 15.4225 | 14.3193 | 13.2239 | 12.5447 | 12.4363 | 12.0365 | 11.485 | 10.9331 | 10.4044 | 9.907 | 9.4316 | 9.001 | 8.628 | 8.2691
VOC as C1 | ppmvd | 5.3254 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
VOC as C1, per MP | lbs/hr | 2.1702 | 2.0493 | 2.06 | 2.0728 | 2.0838 | 2.0907 | 2.0539 | 1.9718 | 1.9089 | 1.846 | 1.7874 | 1.732 | 1.6841 | 1.6387 | 1.593 | 1.5539
SO2 | ppmvd | 9.5203 | 9.5188 | 9.5174 | 9.5159 | 9.5145 | 9.5137 | 9.5141 | 9.5145 | 9.5144 | 9.5143 | 9.5141 | 9.5135 | 9.513 | 9.5121 | 9.5112 | 9.5098
SO2, per MP | lbs/hr | 15.536 | 15.623 | 15.7023 | 15.7969 | 15.8782 | 15.9297 | 15.6498 | 15.025 | 14.5455 | 14.0659 | 13.6189 | 13.1963 | 12.8308 | 12.4839 | 12.1344 | 11.8349
TSP/PM10, Filterable and Cond, per MP | lbs/hr | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Exhaust Gas Flow, per MP ** | lbs/sec | 276.7335 | 273.1178 | 269.5601 | 266.1678 | 262.7613 | 260.7097 | 257.5826 | 249.9484 | 243.0519 | 236.0341 | 229.2994 | 222.7822 | 216.75 | 210.8885 | 205.0223 | 199.4632
Exhaust Gas Temperature ** | Deg F | 599.7798 | 618.3277 | 636.6121 | 655.1992 | 673.555 | 684.8777 | 686.4697 | 692.6611 | 701.8769 | 711.4009 | 721.1126 | 730.8361 | 740.8521 | 750.6136 | 759.7805 | 769.3083
Exhaust Gas Molecular Weight, Wet |  | 28.7432 | 28.7301 | 28.715 | 28.6966 | 28.6741 | 28.6588 | 28.6539 | 28.6351 | 28.6059 | 28.5671 | 28.5158 | 28.4492 | 28.3631 | 28.2539 | 28.117 | 27.9456
Exhaust Gas Vol Flow Rate, per MP ** | ACFS | 7446.4734 | 7481.2643 | 7512.9926 | 7549.0696 | 7581.1038 | 7601.1025 | 7521.6731 | 7343.0033 | 7204.8318 | 7063.7637 | 6931.563 | 6805.9108 | 6697.6033 | 6594.8526 | 6491.4232 | 6403.7896
Stack Exhaust Exit Velocity, per MP ** | FPS | 161.1093 | 161.8621 | 162.5485 | 163.3291 | 164.0222 | 164.4548 | 162.7363 | 158.8707 | 155.8813 | 152.8292 | 149.9689 | 147.2503 | 144.907 | 142.684 | 140.4462 | 138.5502
H2O | % Vol wet | 4.9009 | 5.0742 | 5.2642 | 5.4871 | 5.7456 | 5.9176 | 5.9445 | 6.0816 | 6.3309 | 6.6686 | 7.1212 | 7.7145 | 8.4896 | 9.4752 | 10.7107 | 12.2653
O2 | % Vol wet | 15.944 | 15.8344 | 15.7224 | 15.6008 | 15.4737 | 15.3925 | 15.4119 | 15.4314 | 15.4024 | 15.3551 | 15.2819 | 15.1785 | 15.0312 | 14.8407 | 14.6027 | 14.2918
CO2 | % Vol wet | 2.9825 | 3.0369 | 3.0905 | 3.1461 | 3.2001 | 3.2337 | 3.2151 | 3.1792 | 3.1619 | 3.1444 | 3.1282 | 3.1126 | 3.1011 | 3.0889 | 3.0732 | 3.0617
A | % Vol wet | 0.89559 | 0.89421 | 0.89266 | 0.89082 | 0.88864 | 0.88718 | 0.88685 | 0.88543 | 0.88304 | 0.87983 | 0.87555 | 0.86998 | 0.86272 | 0.85351 | 0.84197 | 0.82748
N2 | % Vol wet | 75.2715 | 75.1548 | 75.0248 | 74.8698 | 74.6865 | 74.5637 | 74.5364 | 74.4171 | 74.2166 | 73.9469 | 73.588 | 73.1194 | 72.5103 | 71.7366 | 70.7665 | 69.5488
* All concentrations corrected to 15% O2
** Secondary Cooling Air Mixed with Primary Exhaust
Guaranteed values are indicated by (G), or | value
All other data are estimates.
PerfCustCpy_Standard-MP_LF_60Hz_13.8kV_0.9Pf_MJ_R0-111308.xls |  |  |  | Sheet-3

## LF_WI_Part-Load
FT-8 MobilePac (Liquid Fuel - WI / DRY)
Estimated Performance and Emissions, Part-Load Data
Standard Mobile Pac - 60Hz, 13.8kV, 0.9Pf (Liquid Fuel)
Configuration: Liquid Fuel, Sea Level, 60%RH, DBAX 62-170 Generator at 50 Hz, 10.5kV, 0.9Pf, WI-42ppmvd, Simple-Cycle.
Performance Data
Fuel Type |  | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid
Number of GT's in Operation | No. | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Water Injection In-Service | Yes / No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Percent of MobilePac Rating | % | 100 | 95 | 85 | 75 | 65 | 50 | 100 | 95 | 85 | 75 | 65 | 50 | 100 | 95 | 85 | 75 | 65 | 50
Ambient Temperature | Deg F | 32 | 32 | 32 | 32 | 32 | 32 | 59 | 59 | 59 | 59 | 59 | 59 | 95 | 95 | 95 | 95 | 95 | 95
Ambient Pressure | Psia | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696
Relative Humidity | % | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Inlet Loss | Inch H20 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Exhaust Loss | Inch H20 | 1.0001 | 1.0001 | 1.0001 | 1.0003 | 0.99986 | 1.0001 | 1.0002 | 0.99965 | 1 | 1 | 1.0001 | 0.99989 | 0.99986 | 1.0002 | 1.0002 | 0.99992 | 1.0001 | 0.99984
Fuel LHV | Btu/lb | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360
Ratio of HHV to LHV |  | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065
Gross Power Output | MWe | 28.5423 | 27.119 | 24.2609 | 21.4068 | 18.5526 | 14.2712 | 25.3228 | 24.0567 | 21.5244 | 18.9921 | 16.4599 | 12.6614 | 21.0717 | 20.0181 | 17.9109 | 15.8038 | 13.6966 | 10.5359
Gross Heat Rate, LHV | Btu/kWhr | 9285.9121 | 9336.323 | 9493.2663 | 9726.937 | 10043.3434 | 10741.0734 | 9589.0666 | 9672.1476 | 9875.439 | 10142.3192 | 10498.9721 | 11670.1731 | 10164.102 | 10269.0018 | 10521.5658 | 10845.0839 | 11286.3611 | 12640.7081
Power Isle Aux Loads | kW | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172
Net Power Output | MWe | 28.3703 | 26.947 | 24.0889 | 21.2348 | 18.3806 | 14.0992 | 25.1508 | 23.8847 | 21.3524 | 18.8201 | 16.2879 | 12.4894 | 20.8997 | 19.8461 | 17.7389 | 15.6318 | 13.5246 | 10.3639
Net Heat Rate, LHV | Btu/kWhr | 9342.2096 | 9395.9158 | 9561.0503 | 9805.7244 | 10137.3259 | 10872.1067 | 9654.6438 | 9741.7992 | 9954.9887 | 10235.0115 | 10609.8411 | 11830.8909 | 10247.7504 | 10358 | 10623.585 | 10964.4147 | 11429.8962 | 12850.4942
Fuel Flow, per MP | lbs/hr | 14435.8 | 13790.4 | 12544.4 | 11341.1 | 10148.7 | 8349.02 | 13225.6 | 12673.2 | 11577.5 | 10491.5 | 9412.42 | 8047.97 | 11665.3 | 11196.4 | 10264.2 | 9335.16 | 8419.65 | 7253.88
Burner Water Injection Flow, per MP | gal/min | 31.0669 | 29.056 | 25.3907 | 22.0298 | 18.8356 | 14.277 | 28.7661 | 27.1219 | 23.9306 | 20.8751 | 17.9367 | 14.7334 | 25.7061 | 24.3144 | 21.5876 | 18.9571 | 16.4618 | 13.6933
Emissions & Exhaust Conditions at Stack Exit, After Addition of Secondary Cooling Air*
NOx | ppmvd | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
NOx, as NO2, per MP | lbs/hr | 50.3326 | 48.0713 | 43.7089 | 39.4984 | 35.3272 | 29.0341 | 46.1136 | 44.18 | 40.3445 | 36.5446 | 32.7694 | 27.9928 | 40.6801 | 39.0382 | 35.7752 | 32.5239 | 29.3213 | 25.2394
CO | ppmvd | 18.1231 | 19.9299 | 23.7151 | 28.3107 | 33.5783 | 45.5984 | 17.1779 | 18.6043 | 21.5304 | 25.6573 | 30.3795 | 35.6588 | 15.9933 | 17.3188 | 20.0806 | 23.3308 | 27.5981 | 31.387
CO, per MP | lbs/hr | 13.223 | 13.8879 | 15.0259 | 16.2098 | 17.1955 | 19.1913 | 11.4827 | 11.9148 | 12.5916 | 13.5919 | 14.431 | 14.4697 | 9.4312 | 9.8006 | 10.4137 | 10.9997 | 11.7303 | 11.4835
VOC as C1 | ppmvd | 5 | 5 | 5 | 6.6511 | 9.9292 | 19.7187 | 5 | 5 | 5 | 5.2832 | 7.9211 | 11.2787 | 5 | 5 | 5 | 5 | 6.2137 | 8.5396
VOC as C1, per MP | lbs/hr | 2.0839 | 1.9903 | 1.8097 | 2.1754 | 2.9046 | 4.7408 | 1.9092 | 1.8292 | 1.6704 | 1.5987 | 2.1494 | 2.6144 | 1.6843 | 1.6163 | 1.4812 | 1.3466 | 1.5087 | 1.7847
SO2 | ppmvd | 9.5145 | 9.5166 | 9.5207 | 9.5249 | 9.5296 | 9.5383 | 9.5145 | 9.516 | 9.5197 | 9.5235 | 9.5282 | 9.5368 | 9.5129 | 9.5145 | 9.5178 | 9.5216 | 9.5257 | 9.5337
SO2, per MP | lbs/hr | 15.8794 | 15.1694 | 13.7988 | 12.4752 | 11.1636 | 9.1839 | 14.5482 | 13.9405 | 12.7353 | 11.5406 | 10.3537 | 8.8528 | 12.8318 | 12.316 | 11.2906 | 10.2687 | 9.2616 | 7.9793
TSP/PM10, Filterable and Cond, per MP | lbs/hr | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Exhaust Gas Flow, per MP ** | lbs/sec | 262.7683 | 258.5653 | 249.2213 | 239.0763 | 228.4393 | 211.3093 | 243.0689 | 238.8389 | 230.0869 | 220.9439 | 211.3779 | 200.8799 | 216.759 | 213.118 | 205.688 | 197.883 | 189.588 | 180.883
Exhaust Gas Temperature ** | Deg F | 673.5716 | 660.7682 | 638.3975 | 618.1618 | 597.4116 | 562.8264 | 701.9238 | 692.3521 | 673.1461 | 653.5698 | 633.1573 | 609.437 | 740.8672 | 731.9844 | 713.7492 | 694.9683 | 676.4399 | 653.0253
Exhaust Gas Molecular Weight, Wet |  | 28.674 | 28.687 | 28.7103 | 28.7318 | 28.7532 | 28.7858 | 28.6059 | 28.6164 | 28.6373 | 28.6581 | 28.679 | 28.7036 | 28.3631 | 28.3726 | 28.3917 | 28.4109 | 28.4296 | 28.4522
Exhaust Gas Vol Flow Rate, per MP ** | ACFS | 7581.4224 | 7372.5288 | 6958.5816 | 6547.398 | 6131.0918 | 5479.5612 | 7205.6383 | 7019.328 | 6644.5241 | 6265.6752 | 5880.177 | 5462.1765 | 6697.9662 | 6534.5563 | 6206.0428 | 5871.029 | 5531.0167 | 5164.192
Stack Exhaust Exit Velocity, per MP ** | FPS | 164.029 | 159.5095 | 150.5535 | 141.6572 | 132.6502 | 118.5539 | 155.8987 | 151.8678 | 143.7586 | 135.562 | 127.2215 | 118.1778 | 144.9149 | 141.3794 | 134.2718 | 127.0236 | 119.6672 | 111.7307
H2O | % Vol wet | 5.746 | 5.5382 | 5.1588 | 4.8005 | 4.4368 | 3.8624 | 6.3316 | 6.1611 | 5.8177 | 5.47 | 5.1133 | 4.6391 | 8.4897 | 8.333 | 8.0129 | 7.6874 | 7.3635 | 6.9176
O2 | % Vol wet | 15.4734 | 15.6397 | 15.9492 | 16.2469 | 16.5549 | 17.0547 | 15.4018 | 15.5405 | 15.8224 | 16.1124 | 16.4142 | 16.8579 | 15.0311 | 15.1611 | 15.4281 | 15.7036 | 15.9821 | 16.405
CO2 | % Vol wet | 3.2003 | 3.1092 | 2.9385 | 2.7732 | 2.6011 | 2.3194 | 3.1623 | 3.0858 | 2.93 | 2.7688 | 2.6002 | 2.3446 | 3.1011 | 3.0291 | 2.8807 | 2.7268 | 2.5704 | 2.3259
A | % Vol wet | 0.88864 | 0.89019 | 0.89301 | 0.89565 | 0.89831 | 0.90247 | 0.88303 | 0.88431 | 0.88685 | 0.88941 | 0.89202 | 0.89537 | 0.86272 | 0.86388 | 0.86624 | 0.86862 | 0.87098 | 0.87411
N2 | % Vol wet | 74.6863 | 74.8174 | 75.0552 | 75.2783 | 75.5033 | 75.855 | 74.2161 | 74.3231 | 74.5379 | 74.7543 | 74.975 | 75.2579 | 72.5103 | 72.608 | 72.8072 | 73.0087 | 73.2081 | 73.4727
* All concentrations corrected to 15% O2
** Secondary Cooling Air Mixed with Primary Exhaust
Guaranteed values are indicated by (G), or | value
All other data are estimates.
PerfCustCpy_Standard-MP_LF_60Hz_13.8kV_0.9Pf_MJ_R0-111308.xls |  |  |  |  | Sheet-4

## LF_DRY_Base-Loads
FT-8 MobilePac (Liquid Fuel - WI / DRY)
Estimated Performance and Emissions, 100% Base-Load Data
Standard Mobile Pac - 60Hz, 13.8kV, 0.9Pf (Liquid Fuel)
Configuration: Liquid Fuel, Sea Level, 60%RH, DBAX 62-170 Generator at 50 Hz, 10.5kV, 0.9Pf, Std. Combustor-DRY, Simple-Cycle.
Performance Data
Fuel Type |  | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid
Number of GT's in Operation | No. | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Water Injection In-Service | Yes / No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No
Percent of MobilePac Rating | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Ambient Temperature | Deg F | -4 | 5 | 14 | 17 | 23 | 32 | 41 | 50 | 59 | 68 | 77 | 86 | 95 | 104 | 113 | 122
Ambient Pressure | Psia | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696
Relative Humidity | % | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Inlet Loss | Inch H20 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5001 | 2.5 | 2.5
Exhaust Loss | Inch H20 | 0.99992 | 0.99973 | 1.0001 | 1.0001 | 1.0001 | 1.0001 | 1.0003 | 0.99981 | 0.99989 | 1.0001 | 1.0001 | 1.0003 | 1.0001 | 0.99992 | 0.99973 | 1.0001
Fuel LHV | Btu/lb | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360
Ratio of HHV to LHV |  | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065
Gross Power Output | MWe | 28.1445 | 28.1708 | 28.1745 | 28.1702 | 27.4126 | 25.8675 | 23.9927 | 22.5595 | 21.3953 | 20.3527 | 19.3703 | 18.4691 | 17.6467 | 16.8608 | 16.0844 | 15.4053
Gross Heat Rate, LHV | Btu/kWhr | 8730.565 | 8766.1459 | 8802.8558 | 8815.4748 | 8867.7556 | 8982.8611 | 9143.4601 | 9299.1066 | 9448.0377 | 9597.9841 | 9756.5254 | 9918.2531 | 10084.3445 | 10259.8674 | 10449.6782 | 10640.107
Power Isle Aux Load | kW | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
Net Power Output | MWe | 28.0305 | 28.0568 | 28.0605 | 28.0562 | 27.2986 | 25.7535 | 23.8787 | 22.4455 | 21.2813 | 20.2387 | 19.2563 | 18.3551 | 17.5327 | 16.7468 | 15.9704 | 15.2913
Net Heat Rate, LHV | Btu/kWhr | 8766.0722 | 8801.7644 | 8838.6187 | 8851.2945 | 8904.7876 | 9022.6245 | 9187.1122 | 9346.3365 | 9650.6274 | 9652.0474 | 9814.2854 | 9979.8535 | 10149.9143 | 10329.7091 | 10524.2701 | 10719.4314
Fuel Flow, per MP | lbs/hr | 13383.3 | 13450.4 | 13508.5 | 13525.8 | 13240.1 | 12656 | 11948.6 | 11426.1 | 11010 | 10639.7 | 10293.4 | 9977.19 | 9692.56 | 9422.09 | 9154.51 | 8927.78
Liquid Fuel Flow, per MP | gal/min | 31.4763 | 31.6341 | 31.7707 | 31.8114 | 31.1395 | 29.7657 | 28.102 | 26.8731 | 25.8945 | 25.0236 | 24.2091 | 23.4654 | 22.796 | 22.1599 | 21.5306 | 20.9973
Burner Water Injection Flow, per MP | gal/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions & Exhaust Conditions at Stack Exit, After Addition of Secondary Cooling Air*
NOx | ppmvd | 355.004 | 377.362 | 404.58 | 413.738 | 414.716 | 410.031 | 400.295 | 399.541 | 403.094 | 407.724 | 412.601 | 417.681 | 423.474 | 428.857 | 432.97 | 437.766
NOx, as NO2, per MP | lbs/hr | 394.368 | 421.398 | 453.842 | 464.745 | 455.991 | 430.914 | 397.115 | 379.014 | 368.463 | 360.171 | 352.628 | 346.027 | 340.847 | 335.584 | 329.221 | 324.677
CO | ppmvd | 21.4121 | 19.5422 | 17.7229 | 17.1266 | 17.0629 | 17.368 | 18.0019 | 18.0511 | 17.8197 | 17.5182 | 17.2007 | 16.8698 | 16.4926 | 16.1421 | 15.8742 | 15.562
CO, per MP | lbs/hr | 14.4819 | 13.2863 | 12.1041 | 11.7127 | 11.4223 | 11.1127 | 10.873 | 10.4254 | 9.9171 | 9.4217 | 8.9501 | 8.5089 | 8.082 | 7.6903 | 7.3488 | 7.027
VOC as C1 | ppmvd | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
VOC as C1, per MP | lbs/hr | 1.9317 | 1.9418 | 1.9507 | 1.9533 | 1.912 | 1.8275 | 1.7251 | 1.6496 | 1.5895 | 1.5361 | 1.4862 | 1.4406 | 1.3996 | 1.3607 | 1.3222 | 1.2897
SO2 | ppmvd | 9.5173 | 9.5152 | 9.5131 | 9.5124 | 9.5128 | 9.5135 | 9.5149 | 9.5153 | 9.5153 | 9.515 | 9.5146 | 9.514 | 9.5132 | 9.5121 | 9.511 | 9.5094
SO2, per MP | lbs/hr | 14.7216 | 14.7954 | 14.8593 | 14.8784 | 14.5641 | 13.9216 | 13.1435 | 12.5687 | 12.111 | 11.7037 | 11.3227 | 10.9749 | 10.6618 | 10.3643 | 10.07 | 9.8206
TSP/PM10, Filterable and Cond, per MP | lbs/hr | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Exhaust Gas Flow, per MP ** | lbs/sec | 272.6265 | 268.9158 | 265.2751 | 264.0715 | 259.6368 | 251.5343 | 242.1666 | 234.1344 | 227.0439 | 220.4391 | 214.1004 | 208.1122 | 202.411 | 196.8495 | 191.3243 | 186.1542
Exhaust Gas Temperature ** | Deg F | 623.5687 | 643.7944 | 663.7067 | 670.2869 | 675.3535 | 680.5215 | 683.8047 | 691.2961 | 700.6987 | 710.5303 | 720.4916 | 730.4817 | 740.7798 | 750.8731 | 760.3609 | 770.1049
Exhaust Gas Molecular Weight, Wet |  | 28.992 | 28.9889 | 28.9838 | 28.9815 | 28.9749 | 28.961 | 28.9434 | 28.9202 | 28.8894 | 28.8487 | 28.7955 | 28.7265 | 28.638 | 28.5256 | 28.3841 | 28.2077
Exhaust Gas Vol Flow Rate, per MP ** | ACFS | 7436.3176 | 7472.8518 | 7506.0272 | 7516.3399 | 7424.9411 | 7229.4596 | 6984.503 | 6802.5365 | 6657.5029 | 6527.7909 | 6405.881 | 6294.5073 | 6194.1149 | 6098.5047 | 6003.5699 | 5924.8096
Stack Exhaust Exit Velocity, per MP ** | FPS | 160.8896 | 161.68 | 162.3978 | 162.6209 | 160.6435 | 156.4141 | 151.1143 | 147.1773 | 144.0394 | 141.233 | 138.5954 | 136.1858 | 134.0137 | 131.9451 | 129.8912 | 128.1871
H2O | % Vol wet | 2.573 | 2.6565 | 2.7576 | 2.7966 | 2.8434 | 2.9295 | 3.0313 | 3.2098 | 3.4706 | 3.8256 | 4.2965 | 4.9128 | 5.7095 | 6.7246 | 8.003 | 9.6039
O2 | % Vol wet | 16.5476 | 16.4575 | 16.3657 | 16.3344 | 16.3432 | 16.3805 | 16.4382 | 16.4461 | 16.4197 | 16.3684 | 16.2915 | 16.1819 | 16.0309 | 15.8344 | 15.5862 | 15.2653
CO2 | % Vol wet | 2.894 | 2.9476 | 2.9997 | 3.0168 | 3.003 | 2.962 | 2.9035 | 2.8697 | 2.8487 | 2.8315 | 2.8152 | 2.8004 | 2.7884 | 2.776 | 2.7611 | 2.7498
A | % Vol wet | 0.91668 | 0.9161 | 0.91536 | 0.91506 | 0.91457 | 0.9136 | 0.91242 | 0.91063 | 0.90811 | 0.90474 | 0.90029 | 0.8945 | 0.88705 | 0.87756 | 0.86561 | 0.85069
N2 | % Vol wet | 77.0433 | 76.9951 | 76.9323 | 76.907 | 76.8659 | 76.7851 | 76.6865 | 76.5359 | 76.3251 | 76.0419 | 75.6685 | 75.1822 | 74.5558 | 73.7589 | 72.7554 | 71.5014
* All concentrations corrected to 15% O2
** Secondary Cooling Air Mixed with Primary Exhaust
Guaranteed values are indicated by (G), or | value
All other data are estimates.
PerfCustCpy_Standard-MP_LF_60Hz_13.8kV_0.9Pf_MJ_R0-111308.xls |  |  |  |  | Sheet-5

## LF_DRY_Part-Load
FT-8 MobilePac (Liquid Fuel - WI / DRY)
Estimated Performance and Emissions, Part-Load Data
Standard Mobile Pac - 60Hz, 13.8kV, 0.9Pf (Liquid Fuel)
Configuration: Liquid Fuel, Sea Level, 60%RH, DBAX 62-170 Generator at 50 Hz, 10.5kV, 0.9Pf, Std. Combustor-DRY, Simple-Cycle.
Performance Data
Fuel Type |  | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid | Liquid
Number of GT's in Operation | No. | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Water Injection In-Service | Yes / No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No
Percent of MobilePac Rating | % | 100 | 95 | 85 | 75 | 65 | 50 | 100 | 95 | 85 | 75 | 65 | 50 | 100 | 95 | 85 | 75 | 65 | 50
Ambient Temperature | Deg F | 32 | 32 | 32 | 32 | 32 | 32 | 59 | 59 | 59 | 59 | 59 | 59 | 95 | 95 | 95 | 95 | 95 | 95
Ambient Pressure | Psia | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696 | 14.696
Relative Humidity | % | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Inlet Loss | Inch H20 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Exhaust Loss | Inch H20 | 1.0002 | 1.0001 | 1.0003 | 1.0001 | 1.0002 | 1.0001 | 0.99997 | 1.0001 | 0.99986 | 1.0003 | 1.0001 | 1.0002 | 1.0001 | 1.0002 | 1.0002 | 1.0001 | 0.99997 | 0.99978
Fuel LHV | Btu/lb | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360 | 18360
Ratio of HHV to LHV |  | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065 | 1.065
Gross Power Output | MWe | 25.8711 | 24.5776 | 21.9904 | 19.4033 | 16.8162 | 12.9355 | 21.3983 | 20.3284 | 18.1885 | 16.0487 | 13.9089 | 10.6991 | 17.6488 | 16.7663 | 15.0014 | 13.2366 | 11.4717 | 8.8244
Gross Heat Rate, LHV | Btu/kWhr | 8982.8886 | 9058.0114 | 9256.8952 | 9519.4603 | 9867.7603 | 10639.7729 | 9447.8285 | 9551.0222 | 9800.8998 | 10119.6048 | 10535.7642 | 11812.3419 | 10083.9768 | 10212.6248 | 10512.371 | 10911.1519 | 11780.94 | 12888.8557
Power Isle Aux Load | kW | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
Net Power Output | MWe | 25.7571 | 24.4636 | 21.8764 | 19.2893 | 16.7022 | 12.8215 | 21.2843 | 20.2144 | 18.0745 | 15.9347 | 13.7949 | 10.5851 | 17.5348 | 16.6523 | 14.8874 | 13.1226 | 11.3577 | 8.7104
Net Heat Rate, LHV | Btu/kWhr | 9022.6465 | 9100.2216 | 9305.1338 | 9575.7204 | 9935.1122 | 10734.3745 | 9498.4316 | 9604.8856 | 9862.7163 | 10192.0024 | 10622.831 | 11939.5591 | 10149.5363 | 10282.5394 | 10592.8693 | 11005.9404 | 11899.1881 | 13057.5429
Fuel Flow, per MP | lbs/hr | 12657.8 | 12125.5 | 11087.3 | 10060.4 | 9038.03 | 7496.23 | 11011.3 | 10575 | 9709.35 | 8845.67 | 7981.53 | 6883.52 | 9693.36 | 9326.14 | 8589.34 | 7866.37 | 7360.97 | 6194.78
Liquid Fuel Flow, per MP | gal/min | 29.77 | 28.518 | 26.0763 | 23.6611 | 21.2566 | 17.6304 | 25.8975 | 24.8714 | 22.8355 | 20.8042 | 18.7718 | 16.1894 | 22.7979 | 21.9342 | 20.2013 | 18.501 | 17.3123 | 14.5695
Burner Water Injection Flow, per MP | gal/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions & Exhaust Conditions at Stack Exit, After Addition of Secondary Cooling Air*
NOx | ppmvd | 410.14 | 383.453 | 343.106 | 302.645 | 267.845 | 217.282 | 403.165 | 380.524 | 344.214 | 306.656 | 273.426 | 247.666 | 423.513 | 402.521 | 363.312 | 329.784 | 326.285 | 270.953
NOx, as NO2, per MP | lbs/hr | 431.087 | 385.988 | 315.328 | 252.267 | 200.465 | 134.749 | 368.572 | 334.01 | 276.998 | 224.725 | 180.708 | 141.029 | 340.907 | 311.668 | 258.968 | 214.974 | 198.928 | 138.904
CO | ppmvd | 17.3609 | 19.0987 | 22.4989 | 27.3813 | 32.6585 | 44.9918 | 17.815 | 19.2894 | 22.3653 | 26.8972 | 31.6814 | 37.2321 | 16.4901 | 17.857 | 20.7173 | 24.1064 | 24.5287 | 32.0639
CO, per MP | lbs/hr | 11.1097 | 11.7047 | 12.589 | 13.8956 | 14.8815 | 16.9876 | 9.9157 | 10.3084 | 10.9577 | 12.0006 | 12.7478 | 12.9079 | 8.0814 | 8.418 | 8.9907 | 9.5672 | 9.1047 | 10.0077
VOC as C1 | ppmvd | 5 | 5 | 5 | 6.0806 | 9.3325 | 19.1203 | 5 | 5 | 5 | 5.8412 | 8.7203 | 12.2992 | 5 | 5 | 5 | 5 | 5 | 8.9551
VOC as C1, per MP | lbs/hr | 1.8277 | 1.7504 | 1.5981 | 1.7627 | 2.4292 | 4.1239 | 1.5897 | 1.5264 | 1.3994 | 1.4887 | 2.0044 | 2.4357 | 1.3998 | 1.3464 | 1.2395 | 1.1335 | 1.0602 | 1.5966
SO2 | ppmvd | 9.5136 | 9.5161 | 9.5209 | 9.526 | 9.5317 | 9.5413 | 9.5152 | 9.5175 | 9.5218 | 9.5268 | 9.5321 | 9.5416 | 9.5131 | 9.5151 | 9.5194 | 9.5239 | 9.5285 | 9.5376
SO2, per MP | lbs/hr | 13.9236 | 13.3381 | 12.196 | 11.0664 | 9.9418 | 8.2459 | 12.1124 | 11.6325 | 10.6803 | 9.7302 | 8.7797 | 7.5719 | 10.6627 | 10.2588 | 9.4483 | 8.653 | 8.0971 | 6.8143
TSP/PM10, Filterable and Cond, per MP | lbs/hr | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Exhaust Gas Flow, per MP ** | lbs/sec | 251.5433 | 247.4693 | 238.7363 | 229.5133 | 219.8453 | 204.0203 | 227.0539 | 223.3779 | 215.8289 | 207.8689 | 199.4769 | 190.3969 | 202.419 | 199.292 | 192.862 | 186.008 | 183.503 | 171.321
Exhaust Gas Temperature ** | Deg F | 680.5772 | 668.6304 | 646.7543 | 625.1032 | 602.7409 | 566.8134 | 700.7323 | 690.9246 | 671.1706 | 651.0971 | 630.1899 | 605.8426 | 740.7935 | 731.6626 | 712.7261 | 694.7367 | 684.9605 | 650.3867
Exhaust Gas Molecular Weight, Wet |  | 28.961 | 28.9597 | 28.9575 | 28.9552 | 28.9529 | 28.9494 | 28.8894 | 28.8883 | 28.8862 | 28.8841 | 28.8819 | 28.8789 | 28.638 | 28.6369 | 28.6347 | 28.6326 | 28.6309 | 28.6273
Exhaust Gas Vol Flow Rate, per MP ** | ACFS | 7230.07 | 7038.7513 | 6659.2249 | 6277.1763 | 5889.2657 | 5281.1639 | 6657.9883 | 6495.0797 | 6168.2869 | 5835.771 | 5495.1729 | 5128.3952 | 6194.4295 | 6052.581 | 5764.6379 | 5474.8631 | 5355.7182 | 4849.7478
Stack Exhaust Exit Velocity, per MP ** | FPS | 156.4273 | 152.288 | 144.0767 | 135.8108 | 127.4181 | 114.2614 | 144.0499 | 140.5253 | 133.4549 | 126.2607 | 118.8917 | 110.9562 | 134.0205 | 130.9516 | 124.7217 | 118.4523 | 115.8745 | 104.9275
H2O | % Vol wet | 2.9297 | 2.8622 | 2.7316 | 2.5984 | 2.4593 | 2.2362 | 3.4708 | 3.4121 | 3.2925 | 3.169 | 3.0399 | 2.844 | 5.7096 | 5.6553 | 5.5428 | 5.4311 | 5.3227 | 5.126
O2 | % Vol wet | 16.38 | 16.4984 | 16.7271 | 16.9603 | 17.2037 | 17.5938 | 16.4194 | 16.5225 | 16.7325 | 16.9495 | 17.1759 | 17.5196 | 16.0307 | 16.1271 | 16.3266 | 16.5249 | 16.7168 | 17.0657
CO2 | % Vol wet | 2.9623 | 2.8852 | 2.7363 | 2.5844 | 2.4258 | 2.1712 | 2.8489 | 2.7818 | 2.645 | 2.5036 | 2.3559 | 2.1316 | 2.7885 | 2.7257 | 2.5955 | 2.4661 | 2.3407 | 2.1128
A | % Vol wet | 0.9136 | 0.91393 | 0.91456 | 0.91519 | 0.91585 | 0.91689 | 0.90811 | 0.90839 | 0.90896 | 0.90955 | 0.91016 | 0.91107 | 0.88705 | 0.8873 | 0.88784 | 0.88836 | 0.88886 | 0.88977
N2 | % Vol wet | 76.785 | 76.8133 | 76.8672 | 76.9218 | 76.9782 | 77.0677 | 76.325 | 76.3494 | 76.3985 | 76.4489 | 76.5012 | 76.5793 | 74.5557 | 74.5781 | 74.6241 | 74.6693 | 74.7119 | 74.7906
* All concentrations corrected to 15% O2
** Secondary Cooling Air Mixed with Primary Exhaust
Guaranteed values are indicated by (G), or | value
All other data are estimates.
PerfCustCpy_Standard-MP_LF_60Hz_13.8kV_0.9Pf_MJ_R0-111308.xls |  |  |  |  | Sheet-6