## Recap
ProEnergy EPC
Job Description: |  |  | "Two Pratt Whitney FT4 Twin Paks SC"
RECAP OF COST ESTIMATE
(1,000'S)
Project Name: |  |  | Barinas I Power Plant |  |  |  |  | Date: | 2010-05-13
Customer: |  |  | PDVSA |  |  |  |  | Quote No: | T 1003 - 3
Location: |  |  | Barinas, Venn |  |  |  |  | Est By: | WTS/DW
Bid Due Date: |  |  | 2010-05-13
I. Balance of Plant | [9 empty] | US $ | BsF
| 100 Civil Structural | [9 empty] | 7
|  | 101 | Site Preparation |  |  |  | 120 | calc
|  | 102 | Excavation - Fill |  |  | Mhrs | 90 | calc
|  | 103 | Concrete Foundations |  |  | 10705.3704 | 1712.8593 | calc
|  | 104 | Concrete Pilings |  |  |  | 0 | calc
|  | 105 | Paving Asphalt - Concrete |  |  |  | 491.5556 | calc
|  | 106 | Gravel - Sand |  |  |  | 119.1204 | calc
|  | 107 | Structual Steel |  |  |  | 85 | calc
|  | 108 | Fencing |  |  |  | 29.7 | calc
|  | 109 | Architectual Treatment |  |  |  | 0 | calc
|  | 110 | Tank Burm / Containment |  |  |  | 175 | calc
[7 empty] | 2823.2352 |  | 2823.2352 | 705.8088 | 14821.9847
| 200 Buildings | [5 empty] | 189 | calc | 189 | 189
| 300 Mechanical |  |  |  |  | Mhrs
|  | 310 | Major Mechanical Equipment |  |  |  | 2895 | calc |  | 2895
|  | 320 | Pipe, Valves & Fitting labor |  |  | 28350 | 1495.1424 | calc |  | 373.7856 | 7849.4977
|  | 330 | Mechanical Subcontractor |  |  | 18238.5 | 961.875 | calc |  | 240.4687 | 5049.8436
|  | 340 | Pipe, Valves & Fitting Material |  |  |  | 750 | calc |  | 750
[7 empty] | 6102.0174 |  | 6102.0174
400 Electrical
|  | 410 | Major Electrical Equipment |  |  |  | 730.8 | calc |  | 730.8
|  | 420 | Substation Equipment |  |  |  | 665 | calc |  | 665
|  | 430 | Plant Electrical Subcontractor |  |  | 13070.7 | 689.3319 | calc |  | 172.333 | 3618.9922
|  | 440 | Substation Subcontractor |  |  | 4860 | 256.3101 | calc |  | 64.0775 | 1345.6282
|  | 450 | Conduit, Cable & Wire Material |  |  |  | 850 | calc |  | 850
|  | 460 | Conduit, Cable & Wire Labor |  |  | 22680 | 1196.1139 | calc |  | 299.0285 | 6279.5982
[7 empty] | 4387.5559 |  | 4387.5559
500 Instrumentation
|  | 510 | CEMS |  |  |  | 0 | calc
|  | 520 | Plant Instrumentation |  |  |  | 120 | calc
|  | 530 | Instrumentation Subcontractor |  |  | 1080 | 56.9578 | calc
[7 empty] | 176.9578 |  | 176.9578 | 176.9578
600 DCS System / Communications
|  | 610 | Hardware / Software |  |  |  | 380 | calc
|  | 620 | Telephone System |  |  |  | 15 | calc
|  | 630 | Public Address System |  |  |  | 15 | calc
|  | 640 | TV / Security |  |  |  | 0 | calc
[7 empty] | 410 |  | 410 | 410
700 Plant Erection
|  | 700 | Plant Erection |  |  | 15012 | 791.7135 | calc
|  | 750 | Plant Dismantling |  |  |  | 0 | plgd/1000
|  | 755 | Plant Dismantling Labor |  |  |  | 0 | plgd/1000
|  |  |  | Total El/Mech Mhrs |  | 103291.2 | 791.7135 |  | 791.7135 | 197.9284 | 4156.496
| 800 Equipment Rental | [5 empty] | 951.1 | calc | 951.1 | 237.775 | 4993.275
| 900 Painting | [5 empty] | 255 | calc | 255 | 63.75 | 1338.75
1000 Transportation
|  | 1001 | US Inland Transportation |  |  |  | 301.822 | calc |  | 301.822
|  | 1002 | Ocean/Air Freight |  |  |  | 600 | plgd /1000 |  | 600
|  | 1003 | Destination Inland Freight |  |  |  | 400 | plgd /1000 |  |  | 2800
|  | 1004 | Customs / Duties (plant equip & mat'l) |  |  |  | 0 | plgd /1000
|  | 1005 | Unload & Receive Mat'l at Site |  |  |  | 0 | plgd /1000
|  | 1006 | Receive, Inspect, Inventory |  |  |  | 0 | plgd /1000
|  | 1007 | Storage |  |  |  | 0 | plgd /1000
|  | 1008 | Local Registrations Fees, License, Etc. |  |  |  | 0 | plgd /1000
|  | 1009 | Transport of Damaged Goods for Repair |  |  |  | 0 | plgd /1000
[7 empty] | 1301.822 |  | 1301.822
| 1100 Site Costs | [5 empty] | 463.8 | calc | 463.8 |  | 3246.6
1200 Engineering
|  | 1201 | EPC Eng Labor |  |  |  | 950 | calc
|  | 1202 | Local Eng |  |  |  | 495 | calc
[7 empty] | 1445 |  | 1445 | 1445
1300 Project Management
|  | 1310 | Project & Construction |  |  |  | 938 | calc
|  | 1320 | Inspectors |  |  |  | 184 | calc
[7 empty] | 1122 |  | 1122 | 1122
| 1400 Travel & Perdiem | [5 empty] | 576.525 | calc
|  | 1410 | Project Meal Expense |  |  |  | 0 | calc
[7 empty] | 576.525 |  | 576.525 | 576.525
| 1500 Technical Reps |  |  |  |  | $/day
|  | 1501 | GTG Tech Rep |  | 200 | 2500 | 500 | plgd /1000
|  | 1502 | Fire Water |  | 0 | 2000 | 0 | plgd /1000
|  | 1503 | Gas Compressor |  | 0 | 2000 | 0 | plgd /1000
|  | 1504 | Chiller |  | 0 | 2000 | 0 | plgd /1000
|  | 1505 | Water Treatment |  | 20 | 2200 | 44 | plgd /1000
|  | 1506 | Commission / S/U / Trng |  | 100 | 2000 | 200 | plgd /1000
|  | 1507 | Controls Rep |  | 30 | 2500 | 75 | plgd /1000
|  | 1508 | DFO Treatment |  | 40 | 2500 | 100 | plgd /1000
|  | 1509 | SCR |  | 0 | 2000 | 0 | plgd /1000
[7 empty] | 919 |  | 919 | 919
1600 Project Tests
|  | 1601 | Soil Boring / Compaction |  |  |  | 20 | plgd /1000
|  | 1602 | Concrete |  |  |  | 40 | plgd /1000
|  | 1603 | X Ray |  |  |  | 40 | plgd /1000
|  | 1604 | Plant Performance and Reliability |  |  |  | 150 | plgd /1000
|  | 1605 | Emission Tests |  |  |  | 0 | plgd /1000
|  | 1606 | Protective Relays |  |  |  | 20 | plgd /1000
|  | 1607 | Acoustics / Noise Test |  |  |  | 0 | plgd /1000
[7 empty] | 270 |  | 270 | 270
| 1700 Legal | [5 empty] | 0 | plgd /1000 | 0
1800 Insurance / Securities
|  | 1810 | Bonds |  |  |  | 0 | plgd /1000
|  | 1820 | Buildiers All Risk |  |  |  | 300 | plgd /1000
|  | 1830 | Marine / Cargo |  |  |  | 0 | plgd /1000
|  | 1840 | Professional |  |  |  | 0 | plgd /1000
[7 empty] | 300 |  | 300 | 300
| 1900 Taxes | [5 empty] | 0 | calc | 0
| 2000 Commissions | [5 empty] | 0 | plgd /1000 | 0
2100 Project Contingency / Risk
|  | 2110 | Project Contingency |  |  |  | 300 | plgd / 1000
|  | 2120 | GT Performance |  |  |  | 0 | plgd / 1000
|  | 2130 | Schedule LD |  |  |  | 0 | plgd / 1000
|  | 2140 | Material Escalation |  | 5% | 6420.8 | 321.04 | calc
|  | 2150 | Labor Contingency |  | 5% | 5447.4446 | 272.3722 | calc
[7 empty] | 893.4122 |  | 893.4122 | 893.4122
[5 empty] | BOP Cost |  |  |  | 23378.1391 | 15449.4725 | 55500.6656
[5 empty] | % Markup |  |  | 25% | 5844.5348 | 5844.5348 | 0
[5 empty] | BOP Sales Price |  |  |  | 29222.6738
[10 empty] | US$ | BsF
[5 empty] | BOP Sales Price Divided |  |  |  |  | 21294.0073 | 55500.6656
[5 empty] | Local Municipal & Social |  |  | 7.5% |  |  | 4162.5499
[5 empty] | IVA |  |  | 16% |  |  | 8880.1065
[5 empty] | Total BOP Price Incl. Taxes |  |  |  |  | 21294.0073 | 68543.322

## 101 Site Prep
|  |  | SITE PREP | [6 empty] | 101
(1,000's)
Project Name: |  | Barinas I Power Plant | [5 empty] | Date: |  | 2010-05-13
Customer: |  | PDVSA | [5 empty] | Quote No: |  | T 1003 - 3
Location: |  | Barinas, Venn | [5 empty] | Est By: |  | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  | "L" | "W" | "D" | Square | Square | Price | Total
No. |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Clearing/Grubbing |  |  | 300 | 450 | 1 | 135000 | 5000 | 24 | 120000
2
3 | Demolition
4
5 | Special Shoring
6
7 | Drainage
8
9 | Dewatering
10
11 | Railroads
12
13 | Docks
14
15 | Tunnels
16
17 | Wells
18
19 | Containment Systems
20
21 | Concrete Work
22
23 | Masonry
24
25
26
27
28
29
30
31
32
33
34
120

## 102 Excavation
|  |  |  | EXCAVATION AND FILL | [6 empty] | 102
(1,000's)
Project Name: |  | Barinas I Power Plant | [6 empty] | Date: |  | 2010-05-13
Customer: |  | PDVSA | [6 empty] | Quote No: |  | T 1003 - 3
Location: |  | Barinas, Venn | [6 empty] | Est By: |  | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Bldg Area
2 | Fuel Gas Compressor Shed |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
3 | Control/Office/Maint |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
4 | Water Treatment Area |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
5 | Electric Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
6 | Pwr Blk Utility Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
7 | Substation Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
8 | Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
9 | Liquid Fuel Unloading Shed |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
10
11 | Main Plant Area |  |  |  | 300 | 450 | 1 | 135000 | 5000 | 18 | 90000
12 | Fill |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
13 | Substation Area |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45 |  |  | Total Cost of Excavation and Fill | [7 empty] | 90

## 103 Foundations
|  |  |  | CONCRETE FOUNDATIONS | [6 empty] | 103
(1,000's)
Project Name: |  | Barinas I Power Plant | [7 empty] | Date: | 2010-05-13
Customer: |  | PDVSA | [7 empty] | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn | [7 empty] | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Price | Total | 5
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price | mhr/cy
1 | POWER ISLAND |  |  | Price: 800
2 | GT Generators FT 4 Twin Pak |  |  | 2 | 105 | 40 | 4 | 33600 | 1244.4444 | 800 | 995555.5556 | 6222.2222
3 | Exhaust Stack |  |  | 0 | 25 | 25 | 4 | 0 | 0 | 800 | 0 | 0
4 | HRSG |  |  | 0 | 75 | 16 | 4 | 0 | 0 | 800 | 0 | 0
5 | SCR |  |  | 0 | 52 | 16 | 4 | 0 | 0 | 800 | 0 | 0
6 | STG |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
7 | STG Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
8 | STG Inlet Chillers |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
9 | STG Condenser Fndn |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
10 | Aux Skid(s) for GTG |  |  | 2 | 30 | 40 | 1 | 2400 | 88.8889 | 800 | 71111.1111 | 444.4444
11
12
13 | BALANCE OF PLANT
14 | Chiller Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
15 | Fuel Gas Regulator Skid |  |  | 0 | 18 | 8 | 1 | 0 | 0 | 800 | 0 | 0
16 | Fuel Gas GTG Meter Skid |  |  | 0 | 25 | 6 | 1 | 0 | 0 | 800 | 0 | 0
17 | Fin Fan L O Coolers |  |  | 0 | 15 | 15 | 2 | 0 | 0 | 800 | 0 | 0
18 | Gas Compressors |  |  | 0 | 45 | 15 | 3 | 0 | 0 | 800 | 0 | 0
19 | Fuel Gas Plant Metering Skid |  |  | 0 | 15 | 8 | 1 | 0 | 0 | 800 | 0 | 0
20 | Comp Fin Fans |  |  | 0 | 15 | 15 | 1 | 0 | 0 | 800 | 0 | 0
21 | Waste Oil/Water Storage Tank |  |  | 1 | 15 | 12 | 1 | 180 | 6.6667 | 800 | 5333.3333 | 33.3333
22 | Oily Water Separator |  |  | 0 | 30 | 20 | 0.5 | 0 | 0 | 800 | 0 | 0
23 | Lubricant Storage Area |  |  | 1 | 45 | 30 | 1 | 1350 | 50 | 800 | 40000 | 250
24 | Instrument Air Comp Skid |  |  | 1 | 10 | 8 | 1 | 80 | 2.963 | 800 | 2370.3704 | 14.8148
25 | Pipe Rack Stanchons |  |  | 20 | 2.5 | 2.5 | 6 | 750 | 27.7778 | 800 | 22222.2222 | 138.8889
26 | 15KV Cable Tray Stanchons |  |  | 10 | 2.5 | 2.5 | 6 | 375 | 13.8889 | 800 | 11111.1111 | 69.4444
27 | Fire Water Pump Skid |  |  | 0 | 15 | 30 | 1 | 0 | 0 | 800 | 0 | 0
28 | Area Light Poles |  |  | 4 | 2.5 | 3 | 5 | 150 | 5.5556 | 800 | 4444.4444 | 27.7778
29 | Aux Trans fndns |  |  | 3 | 10 | 15 | 1.5 | 675 | 25 | 800 | 20000 | 125
30 | Cable Trenches see est |  |  | 2 | 120 | 12 | 0.5 | 1440 | 53.3333 | 800 | 42666.6667 | 266.6667
31 | Water Treatment Plant |  |  | 1 | 30 | 40 | 1 | 1200 | 44.4444 | 800 | 35555.5556 | 222.2222
32 | DFO Unloading Rack |  |  | 1 | 50 | 20 | 1 | 1000 | 37.037 | 800 | 29629.6296 | 185.1852
33 | DFO Forward Pump skid |  |  | 1 | 8 | 6 | 1 | 48 | 1.7778 | 800 | 1422.2222 | 8.8889
34 | DFO Transfer Pump skid |  |  | 1 | 8 | 6 | 1 | 48 | 1.7778 | 800 | 1422.2222 | 8.8889
35 | Demin Water Pump skid |  |  | 1 | 8 | 6 | 1 | 48 | 1.7778 | 800 | 1422.2222 | 8.8889
36 | Demin Stg Tanks ____ Gal |  |  | 2 | 15 | 15 | 1 | 450 | 16.6667 | 800 | 13333.3333 | 83.3333
37 | Demin Forwarding Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
38 | DFO Metering Skid |  |  | 1 | 15 | 6 | 1 | 90 | 3.3333 | 800 | 2666.6667 | 16.6667
39 | Raw Water Tank Base |  |  | 1 | 15 | 15 | 1 | 225 | 8.3333 | 800 | 6666.6667 | 41.6667
40 | Fire Water Tank base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
41 | Emer Generator Base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
42
43 | BUILDINGS
44 | Control Bldg/Office |  |  | 0 | 140 | 60 | 1 | 0 | 0 | 800 | 0 | 0
45 | Warehouse/Maintenance |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
46 | Water Treatment Bldg |  |  | 1 | 30 | 40 | 1 | 1200 | 44.4444 | 800 | 35555.5556 | 222.2222
47 | Gas Compressor Bldg |  |  | 0 | 120 | 45 | 1 | 0 | 0 | 800 | 0 | 0
48 | Electrical Bldg |  |  | 0 | 42 | 20 | 1 | 0 | 0 | 800 | 0 | 0
49 | Pwr Blk Utility Bldg's |  |  | 0 | 30 | 20 | 1 | 0 | 0 | 800 | 0 | 0
50 | Substation Bldg |  |  | 0 | 15 | 12 | 1 | 0 | 0 | 800 | 0 | 0
51 | Steam Turbine Hall |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
52 | Liquid Fuel Unloading |  |  | 1 | 50 | 25 | 1 | 1250 | 46.2963 | 800 | 37037.037 | 231.4815
53 | DFO Treatment Shed |  |  | 1 | 30 | 20 | 1 | 600 | 22.2222 | 800 | 17777.7778 | 111.1111
54 | Control Room |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
55
56 | SUBSTATION
57 | GSU Transformer |  |  | 2 | 30 | 30 | 3 | 5400 | 200 | 800 | 160000 | 1000
58 | (___)KV SF6 Circuit Breaker |  |  | 2 | 15 | 15 | 1 | 450 | 16.6667 | 800 | 13333.3333 | 83.3333
59 | (___)KV Disc Switch w/ Stand |  |  | 2 | 10 | 15 | 1 | 300 | 11.1111 | 800 | 8888.8889 | 55.5556
60 | Dead End Tower |  |  | 0 | 15 | 10 | 3 | 0 | 0 | 800 | 0 | 0
61 | Transmission Line Poles |  |  | 0 | 5 | 5 | 20 | 0 | 0 | 800 | 0 | 0
62 | Insulator Support Base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
63 | PT Support Base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0
64 | GSU Blast Wall |  |  | 2 | 45 | 25 | 2 | 4500 | 166.6667 | 800 | 133333.3333 | 833.3333
65
66
67 |  |  | Total Cost of Foundations | Cubic: 2141.0741; Total: 1712.8593 | 10705.3704
Note on K12: Insert Rate Here:

## 104 Pilings
PILINGS
|  |  |  | (1,000's) | [7 empty] | 104
Project Name: |  | Barinas I Power Plant | [7 empty] | Date: |  | 2010-05-13
Customer: |  | PDVSA | [7 empty] | Quote No: |  | T 1003 - 3
Location: |  | Barinas, Venn | [7 empty] | Est By: |  | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description | [7 empty] | Cu | Price | Total
No. |  |  |  |  | Units | Qty | "L" | "D" | "W" | Yd | CuYd | Price
1 | Concrete Pilings
2 | Pilings GTG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0
3 | Pilings SCR x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Pilings GSU x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Pilings Gas Comp x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Pilings HRSG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Pilings STG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45 |  |  | Total Cost of Retaining Walls |  | Total Price: 0

## 105 Paving
PAVING ASPHALT - CONCRETE
|  |  |  | (1,000's) | [5 empty] | 105
Project Name: |  | Barinas I Power Plant | [6 empty] | Date: | 2010-05-13
Customer: |  | PDVSA | [6 empty] | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn | [6 empty] | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
No. |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Concrete |  |  | 0 | 0 | 0 | 0 | 0 | 600 | 0
2 | Gen Removal Areas |  |  | 60 | 20 | 1 | 1200 | 44.4444 | 600 | 26666.6667
3 | Turbine Removal Areas |  |  | 40 | 20 | 1 | 800 | 29.6296 | 600 | 17777.7778
4 | Entry Ways |  |  | 30 | 8 | 0.5 | 120 | 4.4444 | 600 | 2666.6667
5 | Walk ways |  |  | 0 | 0 | 0 | 0 | 0 | 600 | 0
6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 600 | 0
7
8
9 |  |  |  | "L" | "W" | "D" | Cubic | Cubic | Price
10 | Asphalt |  |  | Ft | Ft | Ft | Ft | Yds | Yd
11 | Roadways |  |  | 1000 | 20 | 0.8 | 20000 | 740.7407 | 600 | 444444.4444
12 | Parking Lot |  |  | 0 | 0 | 0 | 0 | 0 | 600 | 0
13 | [6 empty] | 0 | 0 |  | 0
14 | [6 empty] | 0 | 0 |  | 0
15 | [6 empty] | 0 | 0 |  | 0
16 | [6 empty] | 0 | 0 |  | 0
17 | [6 empty] | 0 | 0 |  | 0
18 | [6 empty] | 0 | 0 |  | 0
19 | [6 empty] | 0 | 0 |  | 0
20 | [6 empty] | 0 | 0 |  | 0
21 | [6 empty] | 0 | 0 |  | 0
22 | [6 empty] | 0 | 0 |  | 0
23 | [6 empty] | 0 | 0 |  | 0
24 | [6 empty] | 0 | 0 |  | 0
25 | [6 empty] | 0 | 0 |  | 0
26 | [6 empty] | 0 | 0 |  | 0
27 | [6 empty] | 0 | 0 |  | 0
28 | [6 empty] | 0 | 0 |  | 0
29 | [6 empty] | 0 | 0 |  | 0
30 | [6 empty] | 0 | 0 |  | 0
31 | [6 empty] | 0 | 0 |  | 0
32 | [6 empty] | 0 | 0 |  | 0
33 | [6 empty] | 0 | 0 |  | 0
34 | [6 empty] | 0 | 0 |  | 0
35 | [6 empty] | 0 | 0 |  | 0
36 | [6 empty] | 0 | 0 |  | 0
37 | [6 empty] | 0 | 0 |  | 0
38 | [6 empty] | 0 | 0 |  | 0
39 | [6 empty] | 0 | 0 |  | 0
40 | [9 empty] | 491.5556
Note on J12: Insert Rate Here:

## 106 Gravel - Sand
GRAVEL
[5 empty] | (1,000's) | [6 empty] | 106
Project Name: |  | Barinas I Power Plant | [7 empty] | Date: |  | 2010-05-13
Customer: |  | PDVSA | [7 empty] | Quote No: |  | T 1003 - 3
Location: |  | Barinas, Venn | [7 empty] | Est By: |  | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Tons | Price | Total
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds |  | /Ton | Price
1
2 | Main Plant Area (less substa) |  |  | 1 | 300 | 450 | 0.5 | 67500 | 2500 | 4150 | 25 | 103750
3
4 | Cooling Tower Area |  |  | 0 | 110 | 160 | 0.5 | 0 | 0 | 0 | 25 | 0
5
6 | Substation |  |  | 0 | 400 | 150 | 1 | 0 | 0 | 0 | 25 | 0
7
8 | Road ways |  |  | 1 | 1000 | 20 | 0.5 | 10000 | 370.3704 | 614.8148 | 25 | 15370.3704
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Gravel | Total: 119.1204

## 107 Structural
STRUCTUAL STEEL
[5 empty] | (1,000's) |  |  |  | 107
Project Name: |  | Barinas I Power Plant | [5 empty] | Date: | 2010-05-13
Customer: |  | PDVSA | [5 empty] | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn | [5 empty] | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | # of | Qty | Price | Total
No. | [5 empty] | Lbs / Tons |  |  | Price
1
2
3 | Misc Pipe Rack supports etc. | [5 empty] | 10 | 3000 | 30000
4 | [8 empty] | 0
5 | 15 KV Cable Tray Stanchons | [5 empty] | 10 | 2500 | 25000
6 | [8 empty] | 0
7 | GTG walkways and stairs | [5 empty] | 2 | 5000 | 10000
8 | [8 empty] | 0
9 | Structual Steel for equip supports | [5 empty] | 0 | 0 | 0
10
11 | Overhead Crane (Bldg) (______) Ton | [5 empty] | 0 | 0 | 0
12
13 | Steel Cover for Storm Water Catch Basin | [5 empty] | 0 | 0 | 0
14
15 | Steel Grating Walkways over pipe ways/ Comp Bldg | [5 empty] | 0 | 0 | 0
16
17 | Misc Walkways, Platforms, & Stairs | [5 empty] | 1 | 20000 | 20000
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41 |  |  | Total Cost of Stuctual Steel | [5 empty] | 85

## 108 Fence
FENCING
[5 empty] | (1,000's) |  |  | 108
Project Name: |  | Barinas I Power Plant |  |  |  |  | Date: | 2010-05-13
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn |  |  |  |  | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | or Ftg | Price | Price
1 | Fencing
2 | Construction Lay Down Area |  |  |  |  | 1500 | 15 | 22500
3 | Site security |  |  |  |  | 0 | 0 | 0
4 | Permanent Site Fence, ___ High w/ ___ Strands Barbed Wire |  |  |  |  | 0 | 0 | 0
5 | Sub Station, ___ High w/ __ Strands Barbed Wire |  |  |  |  | 0 | 0 | 0
6
7
8 | Gates
9 | Manual Double Gate(s) |  |  |  |  | 2 | 3000 | 6000
10 | Motor Operated Double Gate(s) |  |  |  |  | 0 | 0 | 0
11 | Personnel Gate(s) |  |  |  |  | 2 | 600 | 1200
12
13
14 | Intercom Station w/ Remote Button Operation on Gate |  |  |  |  | 0 | 0 | 0
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Fencing |  |  |  |  | 29.7

## 200 Buildings
BUILDINGS
[5 empty] | (1,000's) |  |  |  | 200
Project Name: |  | Barinas I Power Plant | [5 empty] | Date: | 2010-05-13
Customer: |  | PDVSA | [5 empty] | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn | [5 empty] | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  | "L" | "W" | SqFt/ | Price | Total
No. |  |  |  |  | Ft | Ft | or Unit | Ft/Unit | Price
1 | Fuel Gas Compressor Shed |  |  |  | 0 | 0 | 0 | 0 | 0
2 | Control/Office |  |  |  | 0 | 0 | 0 | 0 | 0
3 | Water Treatment |  |  |  | 40 | 40 | 1600 | 45 | 72000
4 | Electric Bldg |  |  |  | 40 | 15 | 600 | 45 | 27000
5 | Warehouse/Maintenance |  |  |  | 0 | 0 | 0 | 0 | 0
6 | Substation Bldg |  |  |  | 0 | 0 | 0 | 0 | 0
7 | Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0
8 | Liquid Fuel Unloading Shed |  |  |  | 55 | 25 | 1375 | 40 | 55000
9 | DFO Treatment Shed |  |  |  | 35 | 25 | 875 | 40 | 35000
10 | Control Room |  |  |  | 0 | 0 | 0 | 0 | 0
11 | Entry Guard House |  |  |  | 0 | 0 | 0 | 0 | 0
12 |  |  |  |  | 0 | 0 | 0 | 0 | 0
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39 |  |  | Total Cost of Other Buildings | [5 empty] | 189

## 310, 320, 330 & 340 Mechanical
MECHANICAL EQUIPMENT and Labor
(1,000's)
310 & 330
Project Name: |  | Barinas I Power Plant | [9 empty] | Date: |  | 2010-05-13
Customer: |  | PDVSA | [9 empty] | Quote No: |  | T 1003 - 3
Location: |  | Barinas, Venn | [9 empty] | Est By: |  | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  |  | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
| GTG |  |  | Unit: 3%; Hours: 9
1 | GTG Type |  |  | 2 | 0 | 0 | 0 | 0 | 9 | 12 | 35 | 7560 | 52.7387 | 398704.6476
2 | Lube oils and Chemicals |  |  | 2 | 50000 | 100000 | 3000 | 6000 | 9 | 0 | 0 | 0 | 52.7387 | 0
3 | Exhaust Stack |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
4 | Project Grouting |  |  | 2 | 55000 | 110000 | 3300 | 6600 | 9 | 0 | 0 | 0 | 52.7387 | 0
5 | GTG Tools |  |  | 1 | 50000 | 50000 | 1500 | 1500 | 9 | 0 | 0 | 0 | 52.7387 | 0
6 | Anchor Bolts |  |  | 2 | 55000 | 110000 | 3300 | 6600 | 9 | 0 | 0 | 0 | 52.7387 | 0
7
8 | HRSG
9 | HRSG Type |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
10 | Duct Burner / FD Fan |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
11 | HP BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
12 | LB BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
13 | Deaerator |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
14 | ByPass Diverter Valve |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
15
16 | SCR
17 | SCR w/ dilution fan, controls, etc. |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
18 | NH2 Tank w/ pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
19
20 | STG
21 | STG |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
22 | Condenser w/ ejectors |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
23 | Condenser Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
24 | Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
25 | CW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
26 | Chemical Inj Skid |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
27
28 | Inlet Air Conditioning System
29 | Inlet Chilling Package |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
30 | Inlet Fogging System |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
31 | Inlet Evap Cooling System |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
32 | Inlet Cooling System Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
33 | Cooling Water Circulation Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
34 | Chilled Water Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
35 | Chemical Inj Skid |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
36
37 | Fuel Gas Systems
38 | Fuel Gas compressor w/ Fin Fans |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
39 | Fuel Gas Check Metering/Regulator Skid |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
40 | Fuel Gas Turbine Metering Skid |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
41 | Fuel Gas Filter Skid & Mnt (___) KW Htr(Htr in Elect) |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
42 | ESD Valve, ___" ___# |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
43
44 | Liquid Fuel Systems
45 | Unloading Pump Skid |  |  | 1 | 25000 | 25000 | 750 | 750 | 9 | 3 | 4 | 108 | 52.7387 | 5695.7807
46 | Metering Skid |  |  | 1 | 155000 | 155000 | 4650 | 4650 | 9 | 3 | 4 | 108 | 52.7387 | 5695.7807
47 | Forwarding Pump Skid |  |  | 1 | 35000 | 35000 | 1050 | 1050 | 9 | 3 | 4 | 108 | 52.7387 | 5695.7807
48 | Transfer Pump Skid |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
49 | Fuel Heating |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
50 | Filter Skid |  |  | 2 | 75000 | 150000 | 4500 | 9000 | 9 | 2 | 4 | 144 | 52.7387 | 7594.3742
51 | Centrifuge |  |  | 2 | 200000 | 400000 | 40000 | 80000 | 9 | 6 | 8 | 864 | 52.7387 | 45566.2454
52 | Injection Pump Skid |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
53 | Raw DFO Storage Tank Cleaning |  |  | 1 | 125000 | 125000 | 3750 | 3750 | 9 | 6 | 10 | 540 | 52.7387 | 28478.9034
54 | Day Tank 600 M Gal CS Coated |  |  | 1 | 400000 | 400000 | 20000 | 20000 | 9 | 6 | 5 | 270 | 52.7387 | 14239.4517
55
56 | Water Supply System
57 | Raw Water Storage Tank 25 M gal |  |  | 1 | 25000 | 25000 | 1500 | 1500 | 9 | 4 | 4 | 144 | 52.7387 | 7594.3742
58 | Raw Water Supply Pumps |  |  | 2 | 15000 | 30000 | 900 | 1800 | 9 | 2 | 3 | 108 | 52.7387 | 5695.7807
59 | Raw Water Forwarding Pumps |  |  | 2 | 15000 | 30000 | 900 | 1800 | 9 | 2 | 3 | 108 | 52.7387 | 5695.7807
60
61 | Water Treatment System
62 | Multi Media Filter Package |  |  | 1 | 45000 | 45000 | 1350 | 1350 | 9 | 3 | 3 | 81 | 52.7387 | 4271.8355
63 | Water Injection Skid |  |  | 0 |  | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
64 | Demin Treatment System 15 M Gal / Day |  |  | 1 | 150000 | 150000 | 4500 | 4500 | 9 | 5 | 6 | 270 | 52.7387 | 14239.4517
65 | Demin Storage SS Tank gal |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
66 | Demin water fiberglass tank |  |  | 1 | 25000 | 25000 | 750 | 750 | 9 | 3 | 6 | 162 | 52.7387 | 8543.671
67 | Demin forwarding pumps |  |  | 1 | 25000 | 25000 | 750 | 750 | 9 | 3 | 4 | 108 | 52.7387 | 5695.7807
68 | Demin Filter Skid |  |  | 1 | 60000 | 60000 | 1800 | 1800 | 9 | 3 | 4 | 108 | 52.7387 | 5695.7807
69 | Demin Water Tank, SS 300M gal |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
70
71 | Waste Water and Oil Storage and Transfer
72 | Oily Water Separator |  |  | 1 | 50000 | 50000 | 1500 | 1500 | 9 | 4 | 3 | 108 | 52.7387 | 5695.7807
73 | Oily Waste Tank 10000 gal |  |  | 1 | 15000 | 15000 | 450 | 450 | 9 | 2 | 3 | 54 | 52.7387 | 2847.8903
74 | Waste Water Tank 10000 gal |  |  | 1 | 15000 | 15000 | 450 | 450 | 9 | 2 | 3 | 54 | 52.7387 | 2847.8903
75 | Waste Oil and Water forwarding pumps w/ skid |  |  | 2 | 10000 | 20000 | 600 | 1200 | 9 | 2 | 3 | 108 | 52.7387 | 5695.7807
76
77 | Fire Control Systems
78 | Fire Water Pump Skids (Diesel / Electric) |  |  | 1 | 550000 | 550000 | 16500 | 16500 | 9 | 4 | 8 | 288 | 52.7387 | 15188.7485
79 | Fire Water System, valves, hydrants, monitors |  |  | 1 | 125000 | 125000 | 3750 | 3750 | 9 | 6 | 12 | 648 | 52.7387 | 34174.6841
80
81 | Storm Water System
82 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
83 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
84 | Sump Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
85
86 | Other Systems
87 | Instrument Air Compressor Package, net (___) scfm |  |  | 1 | 70000 | 70000 | 2100 | 2100 | 9 | 3 | 4 | 108 | 52.7387 | 5695.7807
88 | Potable Water System |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
89 | Anti-Icing Ducting |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
90 | Sanitary Sewer |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
91 |  |  |  | Hours: 9
92
93 |  |  | Total Cost | Total: 2895; Frt: 180.1; Qty: 12159
94 |  |  |  | Total: 641.25
[9 empty] | Total Manhours |  |  | 12159
[9 empty] | Times Prod Factor |  | 1.5 | 18238.5 | 52.7387 | 961.875
95 | BOP Pipe, Valves and Fittings Labor |  |  | 1 | 750000 | 750000 | 22500 | 22500 | 9 | 15 | 140 | 18900 | 52.7387 | 996761.619
96 |  |  | Total Cost | Total: 750; Frt: 22.5; Qty: 18900; Total: 996761.619
97
98 |  |  |  | Hours: Total Manhours; Qty: 18900
99 |  |  |  | Hours: Times Prod Factor; Qty: 1.5; Qty: 28350; Rate: 52.7387; Total: 1495.1424
Price per hour based with all labor burdens as follows:
[8 empty] | Local Hrly Cost |  | 27
[8 empty] | Fringes |  | 2.5
[8 empty] | Small Tools |  | 1.5
[8 empty] | Labor Burden 35% |  | 9.45
40.45
[8 empty] | Contr G&A 8% |  | 3.236
[8 empty] | Contr Mark up 15% |  | 6.0675
49.7535
[7 empty] | 45 | Hour Work Week = |  | 52.7387
Work Week Hours Multiplier
[7 empty] | 45 | 50 | 60
[7 empty] | 1.06 | 1.1 | 1.17
Note on K127: Insert Weekly M/hrs Here: Weekly M/hrs automatically calculated hrs/day.
Note on N119: Insert Rate Here:

## 410, 430, 450 & 460 Electrical
ELECTRICAL EQUIPMENT and Labor
(1,000's)
410, 430, 450 & 460
Project Name: |  | Barinas I Power Plant | [11 empty] | Date: |  | 2010-05-13
Customer: |  | PDVSA | [11 empty] | Quote No: |  | T 1003 - 3
Location: |  | Barinas, Venn | [11 empty] | Est By: |  | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  | Mfgr. | Location | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. | [6 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | Power Island Equipment | [7 empty] | 3% |  | 9
2 | Gas Turbine Generator |  |  |  |  | 2 |  |  | 0 |  | 9 | 9 | 35 | 5670 | 52.7387 | 299028.4857
3 | HRSG |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 52.7387 | 0
4 | SCR |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 52.7387 | 0
5 | STG |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 52.7387 | 0
6 | STG Cooling Tower |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 52.7387 | 0
7 | Chiller Package |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 52.7387 | 0
8 | Water Treatment Package |  |  |  |  | 1 |  |  | 0 |  | 9 | 4 | 7 | 252 | 52.7387 | 13290.1549
9 | [13 empty] | 0 | 52.7387 | 0
10 | 15KV | [13 empty] | 52.7387
11 | Generator Breaker(s) |  |  |  |  | 2 | 135000 | 270000 | 8100 | 16200 | 9 | 4 | 5 | 360 | 52.7387 | 18985.9356
12 | Distribution Breaker(s) |  |  |  |  | 2 | 60000 | 120000 | 3600 | 7200 | 9 | 4 | 4 | 288 | 52.7387 | 15188.7485
13 | Fused Disconnect(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 3 | 4 | 0 | 52.7387 | 0
14 | Bus Duct |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 3 | 4 | 0 | 52.7387 | 0
15 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 4 | 0 | 52.7387 | 0
16 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 6 | 0 | 52.7387 | 0
17 | 5KV | [13 empty] | 52.7387
18 | Distribution Breaker(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 52.7387 | 0
19 | Fused Disconnect(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 6 | 0 | 52.7387 | 0
20 | MCC's |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | 0 | 52.7387 | 0
21 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 6 | 0 | 52.7387 | 0
22 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 52.7387 | 0
23 | 600V | [13 empty] | 52.7387
24 | Distribution Panel(s) |  |  |  |  | 1 | 85000 | 85000 | 2550 | 2550 | 9 | 2 | 5 | 90 | 52.7387 | 4746.4839
25 | GTG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 52.7387 | 0
26 | HRSG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 4 | 0 | 52.7387 | 0
27 | STG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 52.7387 | 0
28 | BOP MCC(s) |  |  |  |  | 1 | 25000 | 25000 | 750 | 750 | 9 | 2 | 3 | 54 | 52.7387 | 2847.8903
29 | Water Treatment MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 0.3 | 0 | 52.7387 | 0
30 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 8 | 0 | 52.7387 | 0
31 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 52.7387 | 0
32 | Aux Transformer(s) | [13 empty] | 52.7387
33 | 15/5KV ___________ MVA |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 52.7387 | 0
34 | 15/600V ___________ MVA |  |  |  |  | 2 | 55000 | 110000 | 3300 | 6600 | 9 | 3 | 5 | 270 | 52.7387 | 14239.4517
35 | 600/120/208V ________ KVA |  |  |  |  | 1 | 5000 | 5000 | 150 | 150 | 9 | 3 | 3 | 81 | 52.7387 | 4271.8355
36 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
37 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
38 | Area Lighting | [13 empty] | 52.7387
39 | Poles _______ High |  |  |  |  | 4 | 1500 | 6000 | 180 | 720 | 9 | 2 | 1 | 72 | 52.7387 | 3797.1871
40 | Floodlights _______ Watts |  |  |  |  | 8 | 600 | 4800 | 144 | 1152 | 9 | 2 | 0.2 | 28.8 | 52.7387 | 1518.8748
41 | [5 empty] | 0 | 0 | 0 |  | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
42 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 60 | 0 | 52.7387 | 0
43 | Other Systems | [13 empty] | 52.7387
44 | UPS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 10 | 0 | 52.7387 | 0
45 | DC |  |  |  |  | 0 | 0 | 0 |  | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
46 | Cathodic Protection |  |  |  |  | 2 | 20000 | 40000 | 1200 | 2400 | 9 | 4 | 8 | 576 | 52.7387 | 30377.497
47 | Lightning Protection |  |  |  |  | 2 | 15000 | 30000 | 900 | 1800 | 9 | 4 | 6 | 432 | 52.7387 | 22783.1227
48 | [11 empty] | 0 | 0 | 0 | 52.7387 | 0
49 | [14 empty] | 52.7387
50 | Temporary Electric |  |  |  |  | 1 | 35000 | 35000 | 1050 | 1050 | 9 | 2 | 30 | 540 | 52.7387 | 28478.9034
51 | Electrical Control Module |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
52 | [6 empty] | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
53 | [6 empty] | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
54 | [6 empty] | 0 | 0 |  | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
55 |  |  | Total Cost of Electrical Equipment |  |  |  |  | 730.8 |  | 40.572 |  |  |  | 8713.8 |  | 459.5546
[12 empty] | Productivity | 1.5 | 13070.7 | 52.7387 | 689.3319
56 | Cable Tray, Conduit, & Cable |  |  |  |  | 1 | 850000 | 850000 | 25500 | 25500 | 9 | 12 | 140 | 15120 | 52.7387 | 797409.2952
57 |  |  | Total Cost of Electrical Equipment |  |  |  |  | 850 |  | 25.5 |  |  |  | 15120 |  | 797.4093
58 | [10 empty] | Total Manhours |  |  | 15120
59 | [10 empty] | Times Prod Factor |  | 1.5 | 22680 | 52.7387 | 1196.1139
Price per hour based with all labor burdens as follows:
[13 empty] | Local Hrly Cost |  | 27
[13 empty] | Fringes |  | 2.5
[13 empty] | Small Tools |  | 1.5
[13 empty] | Labor Burden 35% |  | 9.45
40.45
[13 empty] | Contr G&A 8% |  | 3.236
[13 empty] | Contr Mark up 15% |  | 6.0675
49.7535
[12 empty] | 45 | Hour Work Week = |  | 52.7387
Work Week Hours Multiplier
[12 empty] | 45 | 50 | 60
[12 empty] | 1.06 | 1.1 | 1.17
Note on N87: Insert Weekly M/hrs Here: Automatically calculates hrs/day.
Note on Q79: Insert Rate Here:

## 420 & 440 Substation
SUBSTATION EQUIPMENT and Labor
(1,000's)
Project Name: |  | Barinas I Power Plant | [12 empty] | Date: | 2010-05-13
Customer: |  | PDVSA | [12 empty] | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn | [12 empty] | Est By:
Bid Due Date: |  | 2010-05-13
Item |  | Description |  | Mfgr | Loc | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. | [6 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 |  |  |  | Unit: 3%; Hours: 9
2 | Main Power Transformer _115 KV, _75_ MVA |  |  |  |  | 2 | 0 | 0 | 0 | 0 | 9 | 4 | 10 | 720 | 52.7387 | 37971.8712
3 | SF6 Circuit Breaker(s) ____ KV |  |  |  |  | 2 | 55000 | 110000 | 3300 | 6600 | 9 | 2 | 7 | 252 | 52.7387 | 13290.1549
4 | Disconnect Switches ______ KV |  |  |  |  | 2 | 25000 | 50000 | 1500 | 3000 | 9 | 2 | 5 | 180 | 52.7387 | 9492.9678
5 | Station Post Insulators ____ KV |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 0.05 | 0 | 52.7387 | 0
6 | Insulator Stanchons ______ High |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.5 | 0 | 52.7387 | 0
7 | Insulator Stanchons ______ High |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.4 | 0 | 52.7387 | 0
8 | Dead End Tower(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 5 | 0 | 52.7387 | 0
9 | Alum Bus ______ Dia Lot of Bus and fittings |  |  |  |  | 1 | 125000 | 125000 | 3750 | 3750 | 9 | 6 | 30 | 1620 | 52.7387 | 85436.7102
10 | Alum Bus Conn's |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.1 | 0 | 52.7387 | 0
11 | Alum Bus End Plugs _____ Dia |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.05 | 0 | 52.7387 | 0
12 | Alum Bus Support Clamps |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.1 | 0 | 52.7387 | 0
13 | Alum Bus "V" Conn's |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.08 | 0 | 52.7387 | 0
14 | Static Wire Poles, ____ High |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 1 | 0 | 52.7387 | 0
15 | Area Lighting Poles, ____ High |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 1 | 0 | 52.7387 | 0
16 | Flood Lights, ______ Watts |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 52.7387 | 0
17 | #4/0 Grounding Conductor |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 0.03 | 0 | 52.7387 | 0
18 | 3/4"x10'-0" Ground Rods & Clamps |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.04 | 0 | 52.7387 | 0
19 | #90 Cadweld Shots |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 0.3 | 0 | 52.7387 | 0
20 | Metering CT's & CPT's |  |  |  |  | 2 | 35000 | 70000 | 2100 | 4200 | 9 | 2 | 3 | 108 | 52.7387 | 5695.7807 | 0
21 | Station Metering w/ In & Out Capabilities |  |  |  |  | 1 | 50000 | 50000 | 1500 | 1500 | 9 | 2 | 5 | 90 | 52.7387 | 4746.4839
22 | Station Protective Relay(s) |  |  |  |  | 1 | 50000 | 50000 | 1500 | 1500 | 9 | 2 | 5 | 90 | 52.7387 | 4746.4839
23 | Station RTU |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 52.7387 | 0
24 | 125V DC System |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 52.7387 | 0
25 | Transmission Line Poles |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 2 | 0 | 52.7387 | 0
26 | Transmission Line Strain Insulators |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0 | 0 | 52.7387 | 0 | 0
27 | Cable Bus, Type _____, Size _____ |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 6 | 0 | 52.7387 | 0
28 | Main Power Transformer Oil, ______ Gal |  |  |  |  | 2 | 55000 | 110000 | 3300 | 6600 | 9 | 2 | 5 | 180 | 52.7387 | 9492.9678
29 | Main Power Transformer Dress Out & Test |  |  |  |  | 2 | 50000 | 100000 | 3000 | 6000 | 9 | 2 | 0 | 0 | 52.7387 | 0
30 | Fiber Optic Cable w/ Messenger Cable |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 5 | 0 | 52.7387 | 0 | 0
31 | Fiber Optic Cable Fittings & Terminations |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 52.7387 | 0
32 |  |  |  | Hours: 9; Rate: 52.7387
33 |  |  |  | Hours: 9; Rate: 52.7387
34 |  |  |  | Hours: 9; Rate: 52.7387
35 |  |  |  | Hours: 9; Rate: 52.7387; Total: 0
36 |  |  | Total Cost of Substation Equipment | Total: 665; Frt: 33.15; Qty: 3240; Total: 170.8734
[12 empty] | Total Hours |  | 3240
[12 empty] | Prod Factor | 1.5 | 4860 | 52.7387 | 256.3101
Price per hour based with all labor burdens as follows:
[13 empty] | Local Hrly Cost |  | 27
[13 empty] | Fringes |  | 2.5
[13 empty] | Small Tools |  | 1.5
[13 empty] | Labor Burden 35% |  | 9.45
40.45
[13 empty] | Contr G&A 8% |  | 3.236
[13 empty] | Contr Mark up 15% |  | 6.0675
49.7535
[12 empty] | 45 | Hour Work Week = |  | 52.7387
Work Week Hours Multiplier
[12 empty] | 45 | 50 | 60
[12 empty] | 1.06 | 1.1 | 1.17
Note on N61: Insert Weekly M/hrs Here: Automatically calculates hrs/day.
Note on Q53: Insert Rate Here:

## 520 & 530 Instrumentation
PLANT INSTRUMENTATION
(1,000's)
520 &530
Project Name: |  | Barinas I Power Plant | [8 empty] | Date: | 2010-05-13
Customer: |  | PDVSA | [8 empty] | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn | [8 empty] | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  | Qty | Unit | Total | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  | GTG's | Cost | Cost | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 |  |  |  | Hours: 9
2 | Instrumentation for GTG |  |  | 2 | 35000 | 70000 | 9 | 2 | 10 | 360 | 52.7387 | 18985.9356
3 |  |  |  | Hours: 9; Rate: 52.7387; Total: 0
4 | Instrumentation for SCR |  |  | 0 | 0 | 0 | 9 | 4 | 15 | 0 | 52.7387 | 0
5 |  |  |  | Hours: 9; Rate: 52.7387
6 | Instrumentation for HRSG |  |  | 0 | 0 | 0 | 9 | 4 | 15 | 0 | 52.7387 | 0
7 |  |  |  | Hours: 9; Rate: 52.7387
8 | Instrumentation for Injection Water Treatment |  |  | 1 | 25000 | 25000 | 9 | 2 | 10 | 180 | 52.7387 | 9492.9678
9 |  |  |  | Hours: 9; Rate: 52.7387
10 | Instrumentation for Waste Water Treatment |  |  | 0 | 0 | 0 | 9 | 2 | 10 | 0 | 52.7387 | 0
11 |  |  |  | Hours: 9; Rate: 52.7387
12 | Instrumentation for DFO Treatment |  |  | 1 | 25000 | 25000 | 9 | 4 | 5 | 180 | 52.7387 | 9492.9678
13 |  |  |  | Hours: 9; Rate: 52.7387
14 | Labor to Install CEMS |  |  | 0 | 0 | 0 | 9 | 4 | 5 | 0 | 52.7387 | 0
15 |  |  |  | Hours: 9; Rate: 52.7387
16 |  |  |  | Hours: 9; Rate: 52.7387
17 |  |  |  | Hours: 9; Rate: 52.7387
18 |  |  |  | Hours: 9; Rate: 52.7387
19 |  |  |  | Hours: 9; Rate: 52.7387
20 |  |  |  | Hours: 9; Rate: 52.7387
21 |  |  |  | Hours: 9; Rate: 52.7387
22 |  |  |  | Hours: 9; Rate: 52.7387
23 |  |  | Total Cost of Plant Instrumentation | Total: 120; Qty: 720; Total: 37.9719
[8 empty] | Total Hours |  | 720
[8 empty] | Prod Factor | 1.5 | 1080 | 52.7387 | 56.9578
Price per hour based with all labor burdens as follows:
[9 empty] | Local Hrly Cost |  | 27
[9 empty] | Fringes |  | 2.5
[9 empty] | Small Tools |  | 1.5
[9 empty] | Labor Burden 35% |  | 9.45
40.45
[9 empty] | Contr G&A 8% |  | 3.236
[9 empty] | Contr Mark up 15% |  | 6.0675
49.7535
[8 empty] | 45 | Hour Work Week = |  | 52.7387
Work Week Hours Multiplier
[8 empty] | 45 | 50 | 60
[8 empty] | 1.06 | 1.1 | 1.17
Note on L50: Insert Weekly M/hrs Here: Automatically calculates hr/day.
Note on O42: Inset Rate Here:

## 610, 620, 630 & 640 DCS
DCS
|  |  |  | (1,000's) |  |  |  | 610, 620, 630 & 640
Project Name: |  | Barinas I Power Plant |  |  |  |  | Date: | 2010-05-13
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn |  |  |  |  | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [6 empty] | Cost | Cost
1
2 | DCS Hardware / Software |  |  |  |  | 1 | 275000 | 275000
3
4 | Lot of Misc interconnecting cables etc. |  |  |  |  | 2 | 15000 | 30000
5
6 | Documentation |  |  |  |  | 1 | 75000 | 75000
7
8 |  |  |  |  | Total DCS |  |  | 380
9
10 | PBX Communications System |  |  |  |  | 1 | 15000 | 15
11
12 | Loud Speaker System |  |  |  |  | 1 | 15000 | 15
13
14 | TV / Security System |  |  |  |  | 0 | 20000 | 0
15
16
17
[7 empty] | taxable | 305030

## 700 Erection
PLANT ERECTION
(1,000's)
700
Project Name: |  | Barinas I Power Plant | [6 empty] | Date: | 2010-05-13
Customer: |  | PDVSA | [6 empty] | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn | [6 empty] | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  | No | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  | Units | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 |  |  |  |  | 9
2 | GTG Erection |  |  | 2 | 9 | 12 | 35 | 7560 | 52.7387 | 398704.6476
3 |  |  |  |  | 9 |  |  |  | 52.7387
4 | HRSG Erection |  |  | 0 | 9 | 10 | 60 | 0 | 52.7387 | 0
5 |  |  |  |  | 9 |  |  |  | 52.7387
6 | SCR Erection |  |  | 0 | 9 | 10 | 60 | 0 | 52.7387 | 0
7 |  |  |  |  | 9 |  |  |  | 52.7387
8 | Water Treatment and FW Systems |  |  | 1 | 9 | 5 | 20 | 900 | 52.7387 | 47464.839
9 |  |  |  |  | 9 |  |  |  | 52.7387
10 | DFO Treatment System |  |  | 1 | 9 | 5 | 20 | 900 | 52.7387 | 47464.839
11 |  |  |  |  | 9 |  |  |  | 52.7387
12 | BOP Equip Erection |  |  | 1 | 9 | 6 | 10 | 540 | 52.7387 | 28478.9034
13 |  |  |  |  | 9 |  |  |  | 52.7387
14 | Gas Compressor Erection |  |  | 0 | 9 | 6 | 5 | 0 | 52.7387 | 0
15 |  |  |  |  | 9 |  |  |  | 52.7387
16 | Evap Cooling Erection |  |  | 0 | 9 | 4 | 4 | 0 | 52.7387 | 0
17 |  |  |  |  | 9 |  |  |  | 52.7387
18 | Fire Water Pump Skid |  |  | 1 | 9 | 4 | 3 | 108 | 52.7387 | 5695.7807
19 |  |  |  |  | 9 |  |  |  | 52.7387
20 | STG Erection |  |  | 0 | 9 | 12 | 36 | 0 | 52.7387 | 0
21 |  |  |  |  | 9 |  |  |  | 52.7387
22 | STG Cooling Tower |  |  | 0 | 9 | 8 | 8 | 0 | 52.7387 | 0
23 |  |  |  |  | 9 |  |  |  | 52.7387
24 |  |  |  |  | 9 |  |  |  | 52.7387
25 |  |  | Total Cost of Plant Erection |  |  |  |  | 10008 |  | 527.809
[6 empty] | Total Hours |  | 10008
[6 empty] | Prod Factor | 1.5 | 15012 | 52.7387 | 791.7135
Price per hour based with all labor burdens as follows:
[7 empty] | Local Hrly Cost |  | 27
[7 empty] | Fringes |  | 2.5
[7 empty] | Small Tools |  | 1.5
[7 empty] | Labor Burden 35% |  | 9.45
40.45
[7 empty] | Contr G&A 8% |  | 3.236
[7 empty] | Contr Mark up 15% |  | 6.0675
49.7535
[6 empty] | 45 | Hour Work Week = |  | 52.7387
Work Week Hours Multiplier
[6 empty] | 45 | 50 | 60
[6 empty] | 1.06 | 1.1 | 1.17
Note on J52: Insert Weekly M/hrs Here: Automatically calculates hr/day.
Note on M44: Insert Rate Here:

## 800 Equip rent
EQUIPMENT RENTAL
[5 empty] | (1,000's) |  |  |  |  | 800
Project Name: |  | Barinas I Power Plant | [6 empty] | Date: | 2010-05-13
Customer: |  | PDVSA | [6 empty] | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn | [6 empty] | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | No. | Days | Total | Cost | Total
No. | [5 empty] | Units | Unit | Days | Per Day | Cost
1 | GTG Equip Rental per ea GTG
2 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 2 | 8 | 16 | 8000 | 128000
3 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
4 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 2 | 35 | 70 | 4000 | 280000
5 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
6 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
7 | 2 ea Fork Lifts |  |  |  |  | 0 | 0 | 0 | 70 | 0
8 | 1 ea Man Lift |  |  |  |  | 2 | 35 | 70 | 100 | 7000
9 | 2 ea Welders |  |  |  |  | 5 | 35 | 175 | 100 | 17500
10
11 | HRSG Erection
12 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
13 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
14 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
15 | 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
16 | 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
17 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
18 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
19
20 | SCR/CO
21 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
22 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
23 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
24 | 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
25 | 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
26 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
27 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
28
29 | STG
30 | 1 ea 200 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
31 | 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
32 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1000 | 0
33 | 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
34 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
35 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
36
37 | STG Cooling Tower
38 | 150 Ton Crane |  |  |  |  | 0 | 0 | 0 | 3000 | 0
39 | 40 Ton Crane |  |  |  |  | 0 | 0 | 0 | 1500 | 0
40 | 2ea Fork Lifts |  |  |  |  | 0 | 0 | 0 | 70 | 0
41
42 | Fuel Gas Compressor Rental per Compr Skid
43 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
44 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
45
46 | BOP Equip Rental per ea GTG
47 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
48 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
49 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 1 | 25 | 25 | 4000 | 100000
50 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 120 | 120 | 2500 | 300000
51 | 2 ea Fork Lifts |  |  |  |  | 1 | 120 | 120 | 100 | 12000
52 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
53 | 2 ea Pick ups |  |  |  |  | 2 | 130 | 260 | 80 | 20800
54 | 1 ea Front End Loader / Back Hoe |  |  |  |  | 1 | 90 | 90 | 70 | 6300
55
56 | Substation Equip Rental
57 | 1 ea 200 Ton Crane w/ operator |  |  |  |  | 2 | 5 | 10 | 4000 | 40000
58 | 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
59 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 25 | 25 | 1500 | 37500
60 | 2 ea Man Lifts |  |  |  |  | 1 | 25 | 25 | 80 | 2000
61 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
62 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
63
64
65
66
67
68 |  |  | Total Cost of Plant Equip Rental |  |  |  |  | 981 |  | 951.1

## 900 Paint
PLANT PAINTING
[5 empty] | (1,000's) |  |  | 900
Project Name: |  | Barinas I Power Plant |  |  |  |  | Date: | 2010-05-13
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn |  |  |  |  | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Paint for GTG |  |  |  |  | 2 | 60000 | 120000
3
4 | Paint for STG and Auxiliaries |  |  |  |  | 0 | 60000 | 0
5
6 | Paint for SCR w/ Pipe Racks |  |  |  |  | 0 | 135000 | 0
7
8 | Paint for Pipe Rack etc. |  |  |  |  | 1 | 40000 | 40000
9
10 | Paint for BOP Equipment |  |  |  |  | 1 | 65000 | 65000
11
12 | Paint for Gas Compressor |  |  |  |  | 0 | 15000 | 0
13
14 | Paint for Water Treatment |  |  |  |  | 1 | 15000 | 15000
15
16 | Paint for DFO Treatment |  |  |  |  | 1 | 15000 | 15000
17
18 | Paint for HRSG |  |  |  |  | 0 | 95000 | 0
19
20
21
22
23
24
25
26
27
28
29
30 |  |  | Total Cost of Plant Painting |  |  |  |  | 255

## 1000 Transportation
PLANT TRANSPORTATION
[5 empty] | (1,000's) |  |  | 1000
Project Name: |  | Barinas I Power Plant |  |  |  |  | Date: | 2010-05-13
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn |  |  |  |  | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Transportation of Plant Major Mechanical Equip |  |  |  |  | 1 | 180.1 | 180.1
3
4 | Transportation of Plant Major Electrical Equip |  |  |  |  | 1 | 40.572 | 40.572
5
6 | Transportation Substation Equip |  |  |  |  | 1 | 33.15 | 33.15
7
8 | Transportation of GTG
9
10 | Transportation of SCR
11
12 | Transportation of HRSG
13
14 | Transportation of STG
15
16 | Pipe, Valves & Fittings |  |  |  |  | 1 | 22.5 | 22.5
17
18 | Conduit, Cable & Wire |  |  |  |  | 1 | 25.5 | 25.5
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Plant Transportation |  |  |  |  | 301.822

## 1100 Site Costs
SITE COSTS
[5 empty] | (1,000's) |  |  |  |  | 1100
Project Name: |  | Barinas I Power Plant | [6 empty] | Date: | 2010-05-13
Customer: |  | PDVSA | [6 empty] | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn | [6 empty] | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | No. | No. | Cost | Total | Total
No. | [5 empty] | Units | Mos | Per Mo | Mo Cost | Cost
1 | Monthly Site Costs
2 | Office Trailers |  |  |  |  | 4 | 8 | 2500 | 80000
3 | Porta Potties |  |  |  |  | 4 | 8 | 150 | 4800
4 | Water and Ice |  |  |  |  | 4 | 8 | 500 | 16000
5 | Fed X |  |  |  |  | 1 | 8 | 500 | 4000
6 | Telephone |  |  |  |  | 1 | 8 | 2500 | 20000
7 | Office Supplies |  |  |  |  | 1 | 8 | 1000 | 8000
8 | [6 empty] | 8
9 | Diesel Fuel for Power Generator and Welders |  |  |  |  | 1 | 8 | 3000 | 24000
10 | Misc Items |  |  |  |  | 1 | 8 | 3000 | 24000
11 |  |  | Total Monthly Cost | [5 empty] | 180800
12
13
14
15
16
17
18 | Monthly Site Costs | [5 empty] | 1 | 180800 |  | 180800
19 | One Time Costs
20 | 500 KW Diesel Generator w/ Dist Equip | [8 empty] | 200000
21 | Cad Station | [8 empty] | 5000
22 | Computers | [8 empty] | 10000
23 | Telephone System and Satalite Dish | [8 empty] | 15000
24 | Plotter | [8 empty] | 0
25 | Fax Machine and Printers | [8 empty] | 3000
26 | Misc equip | [8 empty] | 50000
27 | Signs | [8 empty] | 0
28
29
30
31
32 | Total Project Cost = Cost per Month Times Number of Mos
33 | Plus the Project One Time Costs.
34
35 |  |  | Total Cost of Project Site Costs | [6 empty] | 463.8

## 1200 Engineering
ENGINEERING
[5 empty] | (1,000's) |  |  | 1200
Project Name: |  | Barinas I Power Plant |  |  |  |  | Date: | 2010-05-13
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn |  |  |  |  | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Conceptual Engineering |  |  |  |  | 1 | 25000 | 25000
3
4 | Detailed Engineering per GTG |  |  |  |  | 2 | 350000 | 700000
5
6 | Detailed Engineering per HRSG |  |  |  |  | 0 | 0 | 0
7
8 | Detailed Engineering per STG |  |  |  |  | 0 | 0 | 0
9
10 | Detailed Engineering for DFO Treatment |  |  |  |  | 1 | 50000 | 50000
11
12 | Detailed Engineering per Water Treatment |  |  |  |  | 1 | 50000 | 50000
13
14 | Detailed Engineering per Structural Steel |  |  |  |  | 1 | 125000 | 125000
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33 |  |  | Total Cost of Engineering |  |  |  |  | 950

## 1210 Local Engineering
LOCAL ENGINEERING
[5 empty] | (1,000's) |  |  | 1210
Project Name: |  | Barinas I Power Plant |  |  |  |  | Date: | 2010-05-13
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn |  |  |  |  | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Soils & Environmental Eng |  |  |  |  | 1 | 20000 | 20000
3
4 | Civil Engineer |  |  |  |  | 5 | 25000 | 125000
5
6 | Mechanical Engineer |  |  |  |  | 7 | 25000 | 175000
7
8 | Electrical Engineer |  |  |  |  | 7 | 25000 | 175000
9
10 | Other |  |  |  |  | 0 | 0 | 0
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Local Engineering |  |  |  |  | 495

## 1310 & 1320 PM-CM-Insp
PROJECT MANAGEMENT LABOR
|  |  |  | (1,000's) |  |  |  | 1310 & 1320
Project Name: |  | Barinas I Power Plant |  |  |  |  | Date: | 2010-05-13
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn |  |  |  |  | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | No. | Cost | Total
No. | [5 empty] | Mos | Per Mo | Cost
Home Office
1 | Project Mgr Months on Project |  |  |  |  | 5 | 16000 | 80000
2 | Admin Mgr Months on Project |  |  |  |  | 4 | 6000 | 24000
3 | Scheduler |  |  |  |  | 3 | 8000 | 24000
4 | Purchasing Agent |  |  |  |  | 2 | 8000 | 16000
5 | Expediter |  |  |  |  | 0 | 5000 | 0
6 | Home Office Logistic Coordinator |  |  |  |  | 0 | 9000 | 0
7
8
9 | [6 empty] | 144000
10
11
12
13
14
15
16 | Site Construction
17 | Secretary |  |  |  |  | 7 | 4000 | 28000
18 | Construction Mngr |  |  |  |  | 7 | 16000 | 112000
19 | Contract Cost Admin |  |  |  |  | 0 | 10000 | 0
20 | Scheduler |  |  |  |  | 2 | 8000 | 16000
21 | Mechanical Supervisor |  |  |  |  | 6 | 14000 | 84000
22 | Electrical Supervisor |  |  |  |  | 6 | 14000 | 84000
23 | Civil Supervisor |  |  |  |  | 5 | 14000 | 70000
24 | Clerks |  |  |  |  | 8 | 5000 | 40000
25 | Warehousemen |  |  |  |  | 4 | 3000 | 12000
26 | Draftsman |  |  |  |  | 3 | 8000 | 24000
27 | Security |  |  |  |  | 6 | 14000 | 84000
28 | Safety |  |  |  |  | 6 | 12000 | 72000
29 | QA/QC Mngr |  |  |  |  | 6 | 14000 | 84000
30
31
32 | [6 empty] | 710000
33
34 | Commissioning Techs __ ea __ mos x __ |  |  |  |  | 6 | 14000 | 84000
35
36
37
38 | Training |  |  |  |  | 0 | 0 | 0
39
40 |  |  |  |  | Total Project & Construction Management |  |  | 938
41
42
43
44
45 | Inspectors
46 | Civil - Structual __ ea ___ mos |  |  |  |  | 3 | 11500 | 34500
47 | Mechanical __ ea ___ mos |  |  |  |  | 5 | 11500 | 57500
48 | Electrical __ ea ___ mos |  |  |  |  | 5 | 11500 | 57500
49 | Welder __ ea ___ mos | __ ea ___ mos |  |  |  | 3 | 11500 | 34500
50
51 |  |  |  |  | Total Inspectors |  |  | 184000
52

## 1400 & 1410 Travel & Perdiem
PROJECT MGT TVL AND PER DIEM
|  |  |  | (1,000's) |  |  |  | 1400 & 1410
Project Name: |  | Barinas I Power Plant |  |  |  |  | Date: | 2010-05-13
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1003 - 3
Location: |  | Barinas, Venn |  |  |  |  | Est By: | WTS/DW
Bid Due Date: |  | 2010-05-13
Item |  | Description |  |  |  | No. | Cost | Total
No. | [5 empty] | Units | Per Unit | Cost
1
2 | Project & Construciton Management
3 | R T Air Fares |  |  |  |  | 60 | 3000 | 180000
4 | Months of Per Diem at Site (Mgt) |  | Assumes Apartment Rental, meals, etc. |  |  | 60 | 3000 | 180000
5 | Number of Months of Pick Up Trucks |  |  |  |  | 12 | 2500 | 30000
6 | Misc expenditures |  |  |  |  | 1 | 75000 | 75000
7 | Days Per Diem - Lodging & Meals (Techs) |  |  |  |  | 1200 | 52 | 62400
8
9
10
11
12
13 | Engineering
14 | Round Trip Air Fare for Eng Visits to site |  |  |  |  | 12 | 3000 | 36000
15 | Days of Per Diem Cost for Eng Days at Site |  |  |  |  | 75 | 175 | 13125
16 | Auto Rental for Eng Days at Site |  |  |  |  | 0 | 0 | 0
17 | Misc Travel Expentitures |  |  |  |  | 0 | 0 | 0
18
19
20 |  |  |  |  | Total Cost of Project Mgt Tvl and Per Diem |  |  | 576.525
21
22
23
24 | Engineering Meal Expense |  |  |  |  | 0 | 50 | 0 | 0
25
26 | Project Mgt Meal Expense |  |  |  |  | 0 | 50 | 0 | 0
27
28 |  |  |  |  | Total Meal Expense |  |  | 0
29
30
31
32
33
34
35
36