|  | Feature or Item of Design | Information or Comment |
| --- | --- | --- |
| 1 | Physical plant location | Lot Name: Pan Viejo Sector: Nueva Esperanza District: Zorritos Province: Contralmirante Villar Departamento: Tumbes PSAD 56 Survey Points : See reference dwg. No. 08-B |
| 2 | Plant design nominal capacity | Initially 135,000 KW (180,000 KW) |
| 3 | Permitting requirements for engineering and design | CONTRACTOR to follow Peru Regulatory requirements and Statutes. |
| 4 | Operating Mode and Basic Control Philosophy | The expected duty cycle is likely: - Continuous duty, at or near full load 18 hours per day with load reduced only during early morning hours - No peak loading - No fast starts |
| 5 | Site boundary limits | PSAD 56 Survey Points: See reference dwg. No. 08-B |
| 6 | Site improvements required - Site clearing - Cut/fill - Excavating Dewatering - Spoils removal/handling - Internal roads required | - The site will be cleared and used for both equipment storage (construction lay-down) and permanent equipment installation. - Any existing building foundations that interfere with plant construction should be demolished and removed from the site. - It is expected that there may be more than one grade level established on site in order to minimize cut and fill requirements. - Any cut material suitable for fill should be used for fill. The site has a very large ravine that is too deep to fill. Fill will probably require retaining walls. - Any spoils from the cut and fill operation will be stockpiled on site. See reference Geotechnical Investigation Report entitled “BPZ – Gas Power Plant – Caleta La Cruz – Peru”. - Given the elevation of the site, no special dewatering should be required. - Asphalt roads for plant access and heavy equipment maintenance will be incorporated into the design. |
| 7 | Electrical equipment design . | - All electrical equipment for the power facility will be included as part of the CONTRACTOR design, - CONTRACTOR HV interface points will be at the dead end structures; [TO BE DISCUSSED] - The REP substation electrical interconnection equipment along with the expansion of the REP substation should be included as a break out pricing option by the CONTRACTOR. |
| 8 | Grid Voltage | - The power plant will be located at the end of a radial transmission line that is approximately 1250 kilometers north from Lima, the dominant load center. - Peruvian electric system operates at 60 Hz - Transmission voltage is 220 KV |
| 9 | Grid Three-Phase Short circuit MVA and Line to Ground Short Circuit MVA at tie in point (this data is for maximum output only). | - Short Circuit information to be obtained provided (from REP) by BPZ. - BPZ will provide a consultant to assist with HV substation and transmission work. |
| 10 | Three-phase Line to ground short circuit (X/R) at tie inn point. Utility reactance to resistance ratio for a positive sequence and zero sequence impedance. | - Short circuit information to be obtained through BPZ. - BPZ will provide a consultant to assist with HV substation and transmission work.. |
| 11 | Storm drainage system | - CONTRACTOR to perform a drainage study. - Storm drainage system design should use the same drainage design concepts that were used for the gas plant. Reference drawings: BPZ18006Q002A1-Rev. A, 3A1-Rev.A, 4A1-Rev.A, 5A1-Rev. A, 6A1-Rev. B, 7A0-Rev. B, 13A-1-Rev.B - CONTRACTOR to determine if storm water retention ponds are needed. The large wash in the site could be used for retention ponds. |
| 12 | Fuel supply pipelines to utility metering station point of delivery | Reference ‘Upstream Engineering’ drawings: - 4117 Rev. 1 “Mechanical Flow diagram” - 0500 Rev. 0 “Site Plan” - 5423 Rev. 0 “Piping Plan - Gas Metering/Fresh Water” |
| 13 | Wastewater discharge/disposal requirements | - Process wastewater will not be discharged off-site. - Fire water that has the potential to come into contact with oil shall be collected and transported to the oily waste separator. (If firewater system is required) - Water wash water will be collected and trucked offsite. - Condensate will be collected and utilized for SPRINT. - Any additional waste water will be stored in the waste water collection sump. - Potable water will be comprised of bottled water and sanitary sewage will be collected and trucked offsite. - BPZ uses ARPE for managing off site disposal of oily water, waste water and sanitary water. |
| 14 | Turbine-Generators (make and type) | - GE LM-6000, with air-inlet chiller and SPRINT |
| 15 | NOx emissions | - 25ppmvd@15%O2 |
| 16 | Noise level in the normal plant operating areas | - Reference Peru Noise Standard. - Reference Environmental Impact Assessment (EIA) - Near field equipment noise to be 85 dBA. |
| 17 | Plant Elevation Above Sea Level | - The sea shore is about 800 meters (0.5 mile) to the NW. - Existing site elevation is 50 meters. - Gas plant elevation is 47 meters. |
| 18 | Ambient High Temperature | 40 Deg C Reference Tumbes ASHRAE Data |
| 19 | Ambient Low Temperature | 10 Deg C Reference Tumbes ASHRAE Data |
| 20 | Normal Annual Average Ambient Temperature | 25 Deg C Reference Tumbes ASHRAE Data |
| 21 | Relative Humidity | Maximum 100% |
| 22 | Wind | Refer to the EIA document. |
| 23 | Sunshine (monthly) | Refer to the EIA document, Appendix III, “Work Conditions; Ambient Conditions” |
| 24 | Seismic | Use Peru Standards |
| 25 | Rainfall (monthly/annual) | Refer to the EIA document, Appendix III, “Work Conditions; Ambient Conditions” |
| 26 | Owner fuel specifications (fuel conditions available at the tie in point and its properties) | [To be provided by BPZ based on well-head tests.] |
| 27 | GE fuel requirements (pressure, temperature, etc..) | Refer to GE fuel specification |
| 28 | Raw water specifications | Raw water available through gas plant water supply. (Well-water might be available.) |
| 29 | Required codes and standards | - Reference web site below to find regulations, technical and design information regarding the power industry in Peru, http://www.minem.gob.pe/electricidad/normas_inicio.asp - Use Peru standards and supplement with U.S. Standards as applicable. |
| 30 | Combustion Gas Turbine - scope of supply | Reference GE scope of supply |
| 31 | Stack - scope of supply | To be supplied by CONTRACTOR |
| 32 | Air Inlet Cooling System | Chillers - to be provided by BPZ |
| 33 | Building(s) - scope of supply | - One inclusive building for administration, operations, maintenance, and warehousing. The building will include power plant and gas plant personnel. - All electrical gear to be enclosed within conveniently located buildings and designed for tropical marine environment. |
| 34 | HVAC - scope of supply | - Portions of the multi-functional “administration” building and all electrical enclosures. “Dual” (80%) or redundant systems are desired. |
| 35 | Compressed Air System - scope of supply | Separate instrument air and service air systems required. |
| 36 | Fuel System - scope of supply | - Regulation and heating by Others. - Dry gas filters and metering by CONTRACTOR - [To be coordinated with Gas Plant design.] |
| 37 | Fire Protection system - scope of supply | As required by Peruvian authorities having jurisdiction on fire protection. |
| 38 | Utilities - scope of supply - LV Electrical Distribution - Communication - Security - Lighting - Landscaping | - CONTRACTOR to connect to existing 33 KV supply for construction power and plant backup auxiliary supply. - Communications to be via handheld radios. - Phones will be included in offices, control room and any required interconnection to the utility and or OEM supplier. - Security will be via security fence with a camera placed at plant entrance, linked to the control room. - Lighting will be provided by CONTRACTOR for night operation. - Landscaping required by local authorities will be provided by CONTRACTOR and will provide a positive visual impact. |
| 39 | Insulation/Freeze Protection - scope of supply | - Insulation to be provided for heat conservation and personnel protection. - No freeze protection required. |
| 40 | Painting - scope of supply | - For corrosion requirements the site has a “tropical marine atmosphere”. - Appropriate equipment and painting considerations to be taken for operation in this environment. |
| 41 | Electrical requirements - GSU - Aux transformers - Gen breakers - Switchyard - Interconnection line | - CONTRACTOR to supply all electrical equipment except for the GSUs. - The plant will include black start capabilities. CONTRACTOR to supply this equipment. - The plant will include emergency generator. CONTRACTOR to supply this equipment. |
| 42 | Control System – scope of supply | - CONTRACTOR to supply control system to include plant central control, remote operation and communication off site for COES and BPZ. - The control systems will be required to handle any instability presented by the transmission grid. |
| 43 | CEMS – scope of supply | - CONTRACTOR will supply a Continuous Emissions Monitoring System (CEMS) for NOx, CO, O2.. - Include 1 CEMS per unit. CEMS is not required for the black start or emergency generators. |
| 44 | Operator training – scope of supply | CONTRACTOR to provide training for up to 20 people. |
| 45 | Commissioning and Start-Up | - By CONTRACTOR. Scope to be discussed during EPC contract negotiations. |
| 46 | Commercial Testing | - By CONTRACTOR. Scope to be discussed during EPC contract negotiations. |
| 47 | Dust | - Self-cleaning air filters are required for the combustion turbines. (GE scope of supply.) |

| # Equipment | # Number of Components |
| --- | --- |
| Combustion Turbine Generators | 3 – GE Scope of Supply |
| Combustion Inlet Air Cooling (Chiller Coil or Evaporator) | 6 – Supplied by GE |
| Fuel Gas Scrubber/Separator (If required) | 2 |
| Fuel Gas Knockout Pot | 1 |
| Filter Separator (fuel gas systems) | 2 per CT |
| Service Air Compressor | 1 |
| Instrument Air Compressor, with Dryer | 2 |
| Auxiliary Cooling Water Pumps | 2 |
| Service Water Tank | 1 – 48 hours of storage |
| Service Water Pumps | 2 |
| Reverse Osmosis (if required) | Include redundancy as required to allow maintenance without curtailing generation. |
| Reverse Osmosis Product/Evaporator Distillate Water Storage Tanks (if required) | 1 – 90 minutes storage at full flow |
| Demineralizers (if required) | Include redundancy as required to allow maintenance and regeneration without curtailing generation. |
| Demineralizer Feed Pump (if required) | 2 |
| Demineralized Water Make up Pump (if required) | 2 |
| Demineralized Water Tanks (if required) | 1 (size for maximum plant daily usage) |
| Emergency Water Storage Tank Transfer Pump | 2 – 50% each |
| Sump Pumps | 2 – per Sump |
| Lubricating Oil Pump (AC) | 2 per CTG (Part of OEM Package) |
| Lubricating Oil Pump (DC) | 1 per CTG (Part of OEM Package) |
| Lube Oil Cooler (fin fan) | 2 per CTG (Part of OEM Package) |
| Fire Water Storage Tank | 1 - 2 hours of dedicated storage as required by standard. |
| Diesel Fire Pump (if required) | 1 |
| Electric Fire Pump (if required) | 1 |
| Jockey Fire Pump (if required) | 1 |
| GSU Transformers | 1 per 2 CTGs [TO BE DETERMINED] |
| Station Service Transformers | 4 (or 2; TBD) |
| Battery Chargers | 2 per battery bank |
| Uninterruptible Power Supply | 5 – 1 for each unit and 1 for the central control room; with redundant inverter(s) |
| DCS Controllers | 2 per Processor Unit or Workstation Workstations required: 1 - Engineering 2 – Unit Operations 1 – BOP and Gas Plant interface 1 – Plant operations and monitoring 1 – Maintenance, trending , etc. 1 – Electrical Operations, Substation, interconnection, auxiliary power, etc. 1 - interconnection, auxiliaries, etc. 1 – Annunciator, Event logger |
| Station Battery | 5- 1 per unit and 1 for the control room. |
| CEMS | 4 (1 per unit) |
| Diesel Tank | 1 – 8 hour storage |
| Oil Water Separator | 1 |
| Waste Oil Tank | 1 |
| Septic Tank | 1 |
| Administrative/Control Building/Maintenance/Warehouse Building | 1 |
| Electrical Enclosures | As needed |
| HVAC | Dual 80% each for each building or enclosure. |