| CLIENT: | BIE REF. / REPORT No.: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Bariven S.A. c/o PDVSA Services BV President Kennedylaan 19 2517 JK The Hague The Netherlands | I-BA-003/10_18 |  |  |  |  |  |  |  |  |  |  | PAGE 1 OF 4 |  |  |  |  |  |  |
|  | CLIENT P.O. No.: |  |  |  | VISIT No.: |  |  |  |  |  |  | NEXT SCHED. VISIT: |  |  |  |  |  |  |
|  | 5100077213 |  |  |  | 4519D.02 |  |  |  |  |  |  | None |  |  |  |  |  |  |
| VENDOR: | W.O. / REQ No.: |  |  |  | INSPECTOR: |  |  |  |  |  |  | BASE: |  |  |  |  |  |  |
| ProEnergy Services 2001 Adams Road Sedalia, Missouri 65301 | 2232 |  |  |  | Tom Kourtesis |  |  |  |  |  |  | Laval, QC, CANADA |  |  |  |  |  |  |
|  | VENDOR REF. No.: |  |  |  | INSPECTION DATE(S): |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 01 and 02 February 2010 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUB-VENDORS: |  | LOCATION: |  |  |  |  |  |  |  |  | SUB-VENDOR REF. No.: |  |  |  |  |  |  |  |
| Rolls Royce Canada Ltd. |  | Lachine, QC, Canada |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CLIENT P.O. BRIEF MATERIAL DESCRIPTION: |  |  | I-1 | 10 |  | Hrs |  | I-3 | 2.0 | Hrs |  |  |  | I-4 | 170 KMS |  | I-5 | $0 |
|  |  |  | INSPECTION AT: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Rolls Royce Canada Ltd, Lachine, Canada |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUB-ORDER – BRIEF MATERIAL DESCRIPTION: |  |  | ORDER STATUS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rolls Royce Trent 60 DF WLE |  |  | Complete |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| P.O. ITEM | P.O. QTY. | QTY ACC. | QTY REJ. | NARRATIVE | QP STAGE |
| --- | --- | --- | --- | --- | --- |

INSPECTION VISITS OF 01 AND 02 FEBRUARY 2010: SUMMARY: The inspector visited the facilities of Rolls-Royce Canada to attend a meeting with Mr. Mark Currin and to inspect the units presently in the warehouse. The following personnel participated: Mark Currin – Testing and shipping arrangements – Rolls Royce Tom Kourtesis – TPI – BIE representing PDVSA BV Arrangements were made with Mr. Serge Girard to visit the facilities of GTI, located approximately forty (40) km from the Rolls-Royce plant. SPECIFICATIONS AND DRAWINGS: Rolls Royce drawings and Trent testing standard procedures. MATERIALS: Material was 100% received.

All eight (8) modules for each unit were fabricated in-house:

Module 1:	Air Intake and PLC Low Pressure Compressor

Module 2:	ICD System / Inter Compressor Duct

Module 3:	Internal Gear Box

Module 4:	Six Stage High Pressure Compressor

Module 5:	Consisting of three Assemblies / IP Turbine / Static Stage

Module 6:	External Gear Box

Module 7:	Externals

Module 8:	LPT (Low Pressure Turbine) and the Exhaust Case Tail Bearing Housing

VISUAL AND DIMENSIONAL EXAMINATION:

As previously reported, the four (4) engines were completed, tested and packaged per Rolls-Royce applicable procedures.

One (1) engine was shipped to Rolls-Royce Mt. Vernon and the remaining three (3) engines were temporarily stored in a warehouse in Montreal, awaiting completion of shipping arrangements.  The warehouse is heated at a constant temperature of approximately 70ºF and spotless.

Inspection was mainly for external packaging of each unit and as follows:

Engine Tag Number ESN049:

Packaged for Sea Freight

The unit was packaged in an environmental package, especially made and well protected.  There was no access, except by removing or cutting the cover.

The interior appeared very clean.

Built 10 April 2009 to DIS9062 specification – Trent 60 dual fuel WLE

A couple of digital photographs were taken.

Engine Tag Number ESN050:

Packaged for Air Freight

They were inaccessible for inspection as it was packaged in an air freight cocoon.  The steel stand was well build specifically for air freight shipment.  The package was identified with a serial number, a card located at the exterior of the unit.

Built 02 May 2009 to DIS9062 specification – Trent 60 dual fuel WLE

Engine Tag Number ESN051:

Packaged for Air Freight

They were inaccessible for inspection as it was packaged in an air freight cocoon.

Built 19 May 2009 to DIS9062 specification – Trent 60 dual fuel WLE

Per the records reviewed, all three (3) engines have been tested in accordance with Rolls-Royce factory acceptance test and are ready for service.

The environmental package and the two (2) cocoons are the transportation gear managed by Rolls-Royce.

FUNCTION AND PERFORMANCE TESTS:

Per testing certificates, performance testing on the noted wet low emission units had been performed with satis-factory results.  All steps were strictly adhered to without exceptions.  The below listed certificates were included in the package:

- Test Record and Certificate Industrial Trent

- Industrial Trent 60 Site Performance Test Log Sheet

- Release Certificates – 2 pages

- Build Certificate

- Group “A” Parts Engine Build Log A.R. (2)

- Group “B” Parts Engine Build Log

- Industrial Trent Accessory Log Sheet – 4 pages

The inspector requested copies of the testing documentation (certificates) although Ms. Budeanu advised that she did not contact Mr. F. Curren, the responsible party for this project.

Testing certificates were reviewed and the results obtained were acceptable.  There were no deficiencies detected.  It is important to note that the performance testing was not witnessed.

SPECIAL PROCESSES:

Fabrication of modules was not witnessed or inspected.  Finishing and general workmanship was not inspected.

Boroscopic examination was not witnessed, as a routine the operation is witnessed ensuring that no damage occurs during testing especially on the blades.

MARKING AND PACKING:

The units were identified with a card, attached at the exterior.  A serial number is installed in each unit, a stainless steel plate indicating the engine number.

DOCUMENTATION:

The testing certificates were available for each unit with detailed information. Copies of documentation are included with this report.

RELEASE / NON-CONFORMANCE NOTE:

A release will be issued stating that the units themselves could not be inspected as they were sealed inside their packaging.

ATTACHMENTS:

Documentation (44 pages)

Photos have already been sent with the flash report