## Recap
ProEnergy EPC
Job Description: |  |  | "Two LM 6000s w/ Chilling and Substation"
RECAP OF COST ESTIMATE
(1,000'S)
Project Name: |  |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  |  | 2010-05-20
[10 empty] | US$ | BsF
I. Balance of Plant | [10 empty] | 8
100 Civil Structural
|  | 101 | Site Preparation |  |  |  | 102.037 | calc
|  | 102 | Excavation - Fill |  |  | Mhrs | 100 | calc
|  | 103 | Concrete Foundations |  |  | 7537.5 | 1130.625 | calc
|  | 104 | Concrete Pilings |  |  |  | 0 | calc
|  | 105 | Paving Asphalt - Concrete |  |  |  | 258.1944 | calc
|  | 106 | Gravel - Sand |  |  |  | 263.6019 | calc
|  | 107 | Structual Steel |  |  |  | 125.5 | calc
|  | 108 | Fencing |  |  |  | 21.6 | calc
|  | 109 | Architectual Treatment |  |  |  | 0 | calc
|  | 110 | Evaporation Pond |  |  |  | 0 | calc
[7 empty] | 2001.5583 |  | 2001.5583 | 500.3896 | 12009.35
| 200 Buildings | [5 empty] | 296.75 | calc | 296.75 | 296.75
| 300 Mechanical |  |  |  |  | Mhrs
|  | 310 | Major Mechanical Equipment |  |  |  | 7440 | calc |  | 7440
|  | 320 | Pipe, Valves & Fitting labor |  |  | 16200 | 854.3671 | calc |  | 213.5918 | 5126.2026
|  | 330 | Mechanical Subcontractor |  |  | 16051.5 | 846.5354 | calc |  | 211.6339 | 5079.2124
|  | 340 | Pipe, Valves & Fitting Material |  |  |  | 250 | calc |  | 250
[7 empty] | 9390.9025 |  | 9390.9025
400 Electrical
|  | 410 | Major Electrical Equipment |  |  |  | 1489 | calc |  | 1489
|  | 420 | Substation Equipment |  |  |  | 515 | calc |  | 515
|  | 430 | Plant Electrical Subcontractor |  |  | 14269.5 | 752.555 | calc |  | 188.1388 | 4515.3301
|  | 440 | Substation Subcontractor |  |  | 2592 | 136.6987 | calc |  | 34.1747 | 820.1924
|  | 450 | Conduit, Cable & Wire Material |  |  |  | 600 | calc |  | 600
|  | 460 | Conduit, Cable & Wire Labor |  |  | 16200 | 854.3671 | calc |  | 213.5918 | 5126.2026
[7 empty] | 4347.6209 |  | 4347.6209
500 Instrumentation
|  | 510 | CEMS |  |  |  | 0 | calc
|  | 520 | Plant Instrumentation |  |  |  | 125 | calc
|  | 530 | Instrumentation Subcontractor |  |  | 1890 | 76.3896 | calc
[7 empty] | 201.3896 |  | 201.3896 | 201.3896
600 DCS System / Communications
|  | 610 | Hardware / Software |  |  |  | 415 | calc
|  | 620 | Telephone System |  |  |  | 20 | calc
|  | 630 | Public Address System |  |  |  | 20 | calc
|  | 640 | TV / Security |  |  |  | 0 | calc
[7 empty] | 455 |  | 455 | 455
700 Plant Erection
|  | 700 | Plant Erection |  |  | 12555 | 662.1345 | calc
|  | 750 | Plant Dismantling |  |  |  | 0 | plgd/1000
|  | 755 | Plant Dismantling Labor |  |  |  | 0 | plgd/1000
|  |  |  | Total El/Mech Mhrs |  | 79758 | 662.1345 |  | 662.1345 | 165.5336 | 3972.807
| 800 Equipment Rental | [5 empty] | 1136.35 | calc | 1136.35 | 284.0875 | 6818.1
| 900 Painting | [5 empty] | 240 | calc | 240 | 60 | 1440
1000 Transportation
|  | 1001 | US Inland Transportation |  |  |  | 346.55 | calc |  | 346.55
|  | 1002 | Ocean/Air Freight |  |  |  | 600 | plgd /1000 |  | 600
|  | 1003 | Destination Inland Freight |  |  |  | 400 | plgd /1000 |  |  | 3200
|  | 1004 | Customs / Duties (plant equip & mat'l) |  |  |  | 0 | plgd /1000
|  | 1005 | Unload & Receive Mat'l at Site |  |  |  | 150 | plgd /1000 |  |  | 1200
|  | 1006 | Receive, Inspect, Inventory |  |  |  | 150 | plgd /1000 |  | 37.5 | 900
|  | 1007 | Storage |  |  |  | 0 | plgd /1000
|  | 1008 | Local Registrations Fees, License, Etc. |  |  |  | 0 | plgd /1000
|  | 1009 | Transport of Damaged Goods for Repair |  |  |  | 0 | plgd /1000
[7 empty] | 1646.55 |  | 1646.55
| 1100 Site Costs | [5 empty] | 360.5 | calc | 360.5 | 90.125 | 2163
1200 Engineering
|  | 1201 | EPC Eng Labor |  |  |  | 720 | calc
|  | 1202 | Local Eng |  |  |  | 325 | calc
[7 empty] | 1045 |  | 1045 | 1045
1300 Project Management
|  | 1310 | Project & Construction |  |  |  | 1028 | calc
|  | 1320 | Inspectors |  |  |  | 0 | calc
[7 empty] | 1028 |  | 1028 | 1028
| 1400 Travel & Perdiem | [5 empty] | 399.6 | calc
|  | 1410 | Project Meal Expense |  |  |  | 0 | calc
[7 empty] | 399.6 |  | 399.6 | 399.6
| 1500 Technical Reps |  |  |  |  | $/day
|  | 1501 | GTG Tech Rep |  | 320 | 2200 | 704 | plgd /1000
|  | 1502 | Fire Water |  | 0 | 2000 | 0 | plgd /1000
|  | 1503 | Gas Compressor |  | 0 | 2000 | 0 | plgd /1000
|  | 1504 | Chiller |  | 35 | 2500 | 87.5 | plgd /1000
|  | 1505 | Water Treatment |  | 25 | 2000 | 50 | plgd /1000
|  | 1506 | Commission / S/U / Trng |  | 70 | 2000 | 140 | plgd /1000
|  | 1507 | Controls Rep |  | 30 | 2000 | 60 | plgd /1000
|  | 1508 | Liquid Fuel Treatment |  | 20 | 2000 | 40 | plgd /1000
|  | 1509 | SCR |  | 0 | 2000 | 0 | plgd /1000
[7 empty] | 1081.5 |  | 1081.5 | 1081.5
1600 Project Tests
|  | 1601 | Soil Boring / Compaction |  |  |  | 15 | plgd /1000
|  | 1602 | Concrete |  |  |  | 45 | plgd /1000
|  | 1603 | X Ray |  |  |  | 45 | plgd /1000
|  | 1604 | Plant Performance and Reliability |  |  |  | 140 | plgd /1000
|  | 1605 | Emission Tests |  |  |  | 0 | plgd /1000
|  | 1606 | Protective Relays |  |  |  | 20 | plgd /1000
|  | 1607 | Acoustics / Noise Test |  |  |  | 0 | plgd /1000
[7 empty] | 265 |  | 265 | 265
| 1700 Legal | [5 empty] | 0 | plgd /1000 | 0
1800 Insurance / Securities
|  | 1810 | Bonds |  |  |  | 0 | plgd /1000
|  | 1820 | Buildiers All Risk |  |  |  | 200 | plgd /1000
|  | 1830 | Marine / Cargo |  |  |  | 0 | plgd /1000
|  | 1840 | Professional |  |  |  | 0 | plgd /1000
[7 empty] | 200 |  | 200 | 200
| 1900 Taxes | [5 empty] | 0 | calc | 0
| 2000 Commissions | [5 empty] | 0 | plgd /1000 | 0
2100 Project Contingency / Risk
|  | 2110 | Project Contingency |  |  |  | 400 | plgd / 1000
|  | 2120 | GT Performance |  |  |  | 0 | plgd / 1000
|  | 2130 | Schedule LD |  |  |  | 0 | plgd / 1000
|  | 2140 | Material Escalation |  | 3% | 10874 | 326.22 | calc
|  | 2150 | Labor Contingency |  | 5% | 4183.0475 | 209.1524 | calc
[7 empty] | 935.3724 |  | 935.3724 | 935.3724
[5 empty] | BOP Cost |  |  |  | 25693.2282 | 19146.9286 | 52370.3972
[5 empty] | % Markup |  |  | 25% | 6423.3071 | 7000
[5 empty] | BOP Sales Price |  |  |  | 32116.5353 | 26146.9286 | 52370.3972
[5 empty] | Local Municipal & Social |  |  | 7.5% |  |  | 3927.7798
[5 empty] | IVA |  |  | 16% |  |  | 8379.2636
[5 empty] | Total BOP Sales Price Incl. Taxes |  |  |  |  | 26146.9286 | 64677.4406

## 101 Site Prep
|  |  | SITE PREP | [6 empty] | 101
(1,000's)
Project Name: |  | Morichal Power Plant | [5 empty] | Date: |  | 2010-05-19
Customer: |  | PDVSA | [5 empty] | Quote No: |  | T 1016-3
Location: |  | Morichal, Venn | [5 empty] | Est By: |  | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  | "L" | "W" | "D" | Square | Square | Price | Total
No. |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Clearing/Grubbing |  |  | 500 | 300 | 1 | 150000 | 5555.5556 | 18 | 100000
2
3 | Demolition |  |  | 110 | 10 | 3 | 1100 | 40.7407 | 50 | 2037.037
4 | [6 empty] | 0
5 | Special Shoring | [5 empty] | 0
6 | [6 empty] | 0
7 | Drainage | [5 empty] | 0
8 | [6 empty] | 0
9 | Dewatering | [5 empty] | 0
10 | [6 empty] | 0
11 | Railroads
12
13 | Docks
14
15 | Tunnels
16
17 | Wells
18
19 | Containment Systems
20
21 | Concrete Work
22
23 | Masonry
24
25
26
27
28
29
30
31
32
33
34
102.037

## 102 Excavation
|  |  |  | EXCAVATION AND FILL | [6 empty] | 102
(1,000's)
Project Name: |  | Morichal Power Plant | [6 empty] | Date: |  | 2010-05-19
Customer: |  | PDVSA | [6 empty] | Quote No: |  | T 1016-3
Location: |  | Morichal, Venn | [6 empty] | Est By: |  | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Bldg Area
2 | Fuel Gas Compressor Shed |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
3 | Control/Office/Maint |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
4 | Water Treatment Area |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
5 | Electric Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
6 | Pwr Blk Utility Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
7 | Substation Bldg |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
8 | Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
9 | Liquid Fuel Unloading Shed |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
10
11 | Main Plant Area |  |  |  | 500 | 300 | 1 | 150000 | 5555.5556 | 18 | 100000
12 | Fill |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
13 | Substation Area |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45 |  |  | Total Cost of Excavation and Fill | [7 empty] | 100

## 103 Foundations
|  |  |  | CONCRETE FOUNDATIONS | [6 empty] | 103
(1,000's)
Project Name: |  | Morichal Power Plant | [7 empty] | Date: | 2010-05-19
Customer: |  | PDVSA | [7 empty] | Quote No: | T 1016-3
Location: |  | Morichal, Venn | [7 empty] | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Price | Total | 5
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price | mhr/cy
1 | POWER ISLAND |  |  | Price: 750
2 | GT Generators |  |  | 2 | 60 | 20 | 4 | 9600 | 355.5556 | 750 | 266666.6667 | 1777.7778
3 | Exhaust Stack |  |  | 2 | 25 | 25 | 4 | 5000 | 185.1852 | 750 | 138888.8889 | 925.9259
4 | HRSG |  |  | 0 | 75 | 16 | 4 | 0 | 0 | 750 | 0 | 0
5 | SCR |  |  | 0 | 52 | 16 | 4 | 0 | 0 | 750 | 0 | 0
6 | STG |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
7 | STG Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
8 | GTG Inlet Chillers |  |  | 1 | 50 | 35 | 2 | 3500 | 129.6296 | 750 | 97222.2222 | 648.1481
9 | STG Condenser Fndn |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
10 | Aux Skid(s) for GTG |  |  | 2 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
11
12
13 | BALANCE OF PLANT
14 | Chiller Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
15 | Fuel Gas Regulator Skid |  |  | 3 | 18 | 8 | 1 | 432 | 16 | 750 | 12000 | 80
16 | Fuel Gas GTG Meter Skid |  |  | 1 | 25 | 6 | 1 | 150 | 5.5556 | 750 | 4166.6667 | 27.7778
17 | Fin Fan L O Coolers |  |  | 2 | 15 | 15 | 2 | 900 | 33.3333 | 750 | 25000 | 166.6667
18 | Gas Compressors |  |  | 0 | 45 | 15 | 3 | 0 | 0 | 750 | 0 | 0
19 | Fuel Gas Plant Metering Skid |  |  | 0 | 15 | 8 | 1 | 0 | 0 | 750 | 0 | 0
20 | Waste Oil/Water Pumps |  |  | 2 | 6 | 3 | 1 | 36 | 1.3333 | 750 | 1000 | 6.6667
21 | Waste Oil/Water Storage Tank |  |  | 2 | 15 | 12 | 1 | 360 | 13.3333 | 750 | 10000 | 66.6667
22 | Oily Water Separator |  |  | 1 | 30 | 20 | 0.5 | 300 | 11.1111 | 750 | 8333.3333 | 55.5556
23 | Lubricant Storage Area |  |  | 1 | 45 | 30 | 1 | 1350 | 50 | 750 | 37500 | 250
24 | Instrument Air Comp Skid |  |  | 1 | 10 | 8 | 1 | 80 | 2.963 | 750 | 2222.2222 | 14.8148
25 | Pipe Rack Stanchons |  |  | 30 | 2.5 | 2.5 | 6 | 1125 | 41.6667 | 750 | 31250 | 208.3333
26 | 15KV Cable Tray Stanchons |  |  | 4 | 2.5 | 2.5 | 6 | 150 | 5.5556 | 750 | 4166.6667 | 27.7778
27 | Foam Water Pump Skid |  |  | 1 | 15 | 20 | 1 | 300 | 11.1111 | 750 | 8333.3333 | 55.5556
28 | Area Light Poles |  |  | 5 | 2.5 | 3 | 5 | 187.5 | 6.9444 | 750 | 5208.3333 | 34.7222
29 | Aux Trans fndns |  |  | 4 | 10 | 15 | 1.5 | 900 | 33.3333 | 750 | 25000 | 166.6667
30 | Cable Trenches see est |  |  | 2 | 120 | 15 | 0.5 | 1800 | 66.6667 | 750 | 50000 | 333.3333
31 | Water Treatment Plant |  |  | 1 | 40 | 30 | 0.7 | 840 | 31.1111 | 750 | 23333.3333 | 155.5556
32 | Diesel Fuel Unloading Station |  |  | 0 | 60 | 25 | 1 | 0 | 0 | 750 | 0 | 0
33 | Deisel Fuel Treatment Plant |  |  | 1 | 40 | 30 | 1 | 1200 | 44.4444 | 750 | 33333.3333 | 222.2222
34 | Diesel Fuel Forwarding Skid |  |  | 2 | 8 | 4 | 1 | 64 | 2.3704 | 750 | 1777.7778 | 11.8519
35 | Demin Water Pump skid |  |  | 2 | 6 | 4 | 1 | 48 | 1.7778 | 750 | 1333.3333 | 8.8889
36 | Demin Stg Tanks 25 M Gal |  |  | 4 | 15 | 15 | 1 | 900 | 33.3333 | 750 | 25000 | 166.6667
37 | Demin Forwarding Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
38 | Chemical Injection Skid |  |  | 1 | 12 | 10 | 1 | 120 | 4.4444 | 750 | 3333.3333 | 22.2222
39 | Raw Water Tank Base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
40 | Fire Water Tank base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
41 | Emer Generator Base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
42
43 | BUILDINGS
44 | Control Bldg/Office |  |  | 0 | 140 | 60 | 1 | 0 | 0 | 750 | 0 | 0
45 | Warehouse/Maintenance |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
46 | Water Treatment Bldg |  |  | 1 | 50 | 40 | 1 | 2000 | 74.0741 | 750 | 55555.5556 | 370.3704
47 | Gas Compressor Bldg |  |  | 0 | 120 | 45 | 1 | 0 | 0 | 750 | 0 | 0
48 | Pwr Blk Shed |  |  | 1 | 42 | 30 | 1 | 1260 | 46.6667 | 750 | 35000 | 233.3333
49 | Pwr Blk Utility Bldg's |  |  | 1 | 50 | 45 | 1 | 2250 | 83.3333 | 750 | 62500 | 416.6667
50 | Substation Bldg |  |  | 0 | 15 | 12 | 1 | 0 | 0 | 750 | 0 | 0
51 | Steam Turbine Hall |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
52 | Liquid Fuel Unloading |  |  | 1 | 60 | 25 | 1 | 1500 | 55.5556 | 750 | 41666.6667 | 277.7778
53 | Pump Room(s) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
54 | Control Room |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
55
56 | SUBSTATION
57 | GSU Transformer |  |  | 2 | 30 | 30 | 2 | 3600 | 133.3333 | 750 | 100000 | 666.6667
58 | (___)KV SF6 Circuit Breaker |  |  | 2 | 15 | 15 | 1 | 450 | 16.6667 | 750 | 12500 | 83.3333
59 | (___)KV Disc Switch w/ Stand |  |  | 2 | 10 | 15 | 1 | 300 | 11.1111 | 750 | 8333.3333 | 55.5556
60 | Dead End Tower |  |  | 0 | 15 | 10 | 3 | 0 | 0 | 750 | 0 | 0
61 | Transmission Line Poles |  |  | 0 | 5 | 5 | 20 | 0 | 0 | 750 | 0 | 0
62 | Insulator Support Base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
63 | PT Support Base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
64 | Static Pole Base |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0
65
66
67 |  |  | Total Cost of Foundations | Cubic: 1507.5; Total: 1130.625 | 7537.5
Note on K12: Insert Rate Here:

## 104 Pilings
PILINGS
|  |  |  | (1,000's) | [7 empty] | 104
Project Name: |  | Morichal Power Plant | [7 empty] | Date: |  | 2010-05-19
Customer: |  | PDVSA | [7 empty] | Quote No: |  | T 1016-3
Location: |  | Morichal, Venn | [7 empty] | Est By: |  | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description | [7 empty] | Cu | Price | Total
No. |  |  |  |  | Units | Qty | "L" | "D" | "W" | Yd | CuYd | Price
1 | Concrete Pilings
2 | Pilings GTG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0
3 | Pilings SCR x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Pilings GSU x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Pilings Gas Comp x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Pilings HRSG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Pilings STG x _____ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45 |  |  | Total Cost of Retaining Walls |  | Total Price: 0

## 105 Paving
PAVING ASPHALT - CONCRETE
|  |  |  | (1,000's) | [5 empty] | 105
Project Name: |  | Morichal Power Plant | [6 empty] | Date: | 2010-05-19
Customer: |  | PDVSA | [6 empty] | Quote No: | T 1016-3
Location: |  | Morichal, Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
No. |  |  |  | Ft | Ft | Ft | Ft | Yds | Yd | Price
1 | Concrete |  |  | 0 | 0 | 0 | 0 | 0 | 650 | 0
2 | Gen Removal Areas |  |  | 40 | 20 | 1 | 800 | 29.6296 | 650 | 19259.2593
3 | Turbine Removal Areas |  |  | 30 | 15 | 1 | 450 | 16.6667 | 650 | 10833.3333
4 | Entry Ways |  |  | 15 | 10 | 0.5 | 75 | 2.7778 | 650 | 1805.5556
5 | Walk ways |  |  | 80 | 5 | 0.5 | 200 | 7.4074 | 650 | 4814.8148
6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 650 | 0
7
8
9 |  |  |  | "L" | "W" | "D" | Cubic | Cubic | Price
10 | Asphalt |  |  | Ft | Ft | Ft | Ft | Yds | Yd
11 | Roadways |  |  | 300 | 20 | 0.7 | 6000 | 222.2222 | 650 | 144444.4444
12 | Parking Lot |  |  | 80 | 40 | 0.7 | 3200 | 118.5185 | 650 | 77037.037
13 | [6 empty] | 0 | 0 |  | 0
14 | [6 empty] | 0 | 0 |  | 0
15 | [6 empty] | 0 | 0 |  | 0
16 | [6 empty] | 0 | 0 |  | 0
17 | [6 empty] | 0 | 0 |  | 0
18 | [6 empty] | 0 | 0 |  | 0
19 | [6 empty] | 0 | 0 |  | 0
20 | [6 empty] | 0 | 0 |  | 0
21 | [6 empty] | 0 | 0 |  | 0
22 | [6 empty] | 0 | 0 |  | 0
23 | [6 empty] | 0 | 0 |  | 0
24 | [6 empty] | 0 | 0 |  | 0
25 | [6 empty] | 0 | 0 |  | 0
26 | [6 empty] | 0 | 0 |  | 0
27 | [6 empty] | 0 | 0 |  | 0
28 | [6 empty] | 0 | 0 |  | 0
29 | [6 empty] | 0 | 0 |  | 0
30 | [6 empty] | 0 | 0 |  | 0
31 | [6 empty] | 0 | 0 |  | 0
32 | [6 empty] | 0 | 0 |  | 0
33 | [6 empty] | 0 | 0 |  | 0
34 | [6 empty] | 0 | 0 |  | 0
35 | [6 empty] | 0 | 0 |  | 0
36 | [6 empty] | 0 | 0 |  | 0
37 | [6 empty] | 0 | 0 |  | 0
38 | [6 empty] | 0 | 0 |  | 0
39 | [6 empty] | 0 | 0 |  | 0
40 | [9 empty] | 258.1944
Note on J12: Insert Rate Here:

## 106 Gravel - Sand
GRAVEL
[5 empty] | (1,000's) | [6 empty] | 106
Project Name: |  | Morichal Power Plant | [7 empty] | Date: |  | 2010-05-19
Customer: |  | PDVSA | [7 empty] | Quote No: |  | T 1016-3
Location: |  | Morichal, Venn | [7 empty] | Est By: |  | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  | Qty | "L" | "W" | "D" | Cubic | Cubic | Tons | Price | Total
No. |  |  |  |  | Ft | Ft | Ft | Ft | Yds |  | /Ton | Price
1
2 | Main Plant Area (less substa) |  |  | 1 | 500 | 350 | 0.5 | 87500 | 3240.7407 | 5379.6296 | 25 | 134490.7407
3
4 | Cooling Tower Area |  |  | 0 | 110 | 160 | 0.5 | 0 | 0 | 0 | 25 | 0
5
6 | Substation |  |  | 0 | 400 | 150 | 1 | 0 | 0 | 0 | 25 | 0
7
8 | Road ways |  |  | 300 | 20 | 20 | 0.7 | 84000 | 3111.1111 | 5164.4444 | 25 | 129111.1111
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Gravel | Total: 263.6019

## 107 Structural
STRUCTUAL STEEL
[5 empty] | (1,000's) |  |  |  | 107
Project Name: |  | Morichal Power Plant | [5 empty] | Date: | 2010-05-19
Customer: |  | PDVSA | [5 empty] | Quote No: | T 1016-3
Location: |  | Morichal, Venn | [5 empty] | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | # of | Qty | Price | Total
No. | [5 empty] | Lbs / Tons |  |  | Price
1
2
3 | Misc Pipe Rack supports etc. |  |  |  |  | 0 | 15 | 3000 | 45000
4 | [8 empty] | 0
5 | 15 KV Cable Tray Stanchons | [5 empty] | 5 | 2500 | 12500
6 | [8 empty] | 0
7 | GTG walkways and stairs | [5 empty] | 2 | 15000 | 30000
8 | [8 empty] | 0
9 | Structual Steel for equip supports | [5 empty] | 1 | 30000 | 30000
10
11 | Overhead Crane (Bldg) (______) Ton | [5 empty] | 0 | 0 | 0
12
13 | Steel Cover for Storm Water Catch Basin | [5 empty] | 0 | 0 | 0
14
15 | Steel Grating Walkways over pipe ways/ Comp Bldg | [5 empty] | 0 | 0 | 0
16
17 | Misc Walkways, Platforms, & Stairs | [5 empty] | 1 | 8000 | 8000
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41 |  |  | Total Cost of Stuctual Steel | [5 empty] | 125.5

## 108 Fence
FENCING
[5 empty] | (1,000's) |  |  | 108
Project Name: |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | or Ftg | Price | Price
1 | Fencing
2 | Construction Lay Down Area |  |  |  |  | 1200 | 18 | 21600
3 | Site security |  |  |  |  | 0 | 0 | 0
4 | Permanent Site Fence, ___ High w/ ___ Strands Barbed Wire |  |  |  |  | 0 | 0 | 0
5 | Sub Station, ___ High w/ __ Strands Barbed Wire |  |  |  |  | 0 | 0 | 0
6
7
8 | Gates
9 | Manual Double Gate(s) |  |  |  |  | 0 | 0 | 0
10 | Motor Operated Double Gate(s) |  |  |  |  | 0 | 0 | 0
11 | Personnel Gate(s) |  |  |  |  | 0 | 0 | 0
12
13
14 | Intercom Station w/ Remote Button Operation on Gate |  |  |  |  | 0 | 0 | 0
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Fencing |  |  |  |  | 21.6

## 109 Architectual
ARCHITECTUAL TREATMENT
[5 empty] | (1,000's) |  |  | 109
Project Name: |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | or Ftg | Price | Price
1
2 | Trees and/or Shrubs - Revegetation
3 | Boundry Road |  |  |  |  | 0 | 0 | 0
4 | Within site |  |  |  |  | 0 | 0 | 0
5 | [5 empty] | 0 | 0 | 0
6 | [5 empty] | 0 | 0 | 0
7 | [5 empty] | 0 | 0 | 0
8 | [7 empty] | 0
9 | [7 empty] | 0
10 | [7 empty] | 0
11 | [7 empty] | 0
12 | [7 empty] | 0
13 | [7 empty] | 0
14 | [7 empty] | 0
15 | [7 empty] | 0
16 | [7 empty] | 0
17 | [7 empty] | 0
18 | [7 empty] | 0
19 | [7 empty] | 0
20 | [7 empty] | 0
21 | [7 empty] | 0
22 | [7 empty] | 0
23 | [7 empty] | 0
24 | [7 empty] | 0
25 | [7 empty] | 0
26 | [7 empty] | 0
27 | [7 empty] | 0
28 | [7 empty] | 0
29 | [7 empty] | 0
30 | [7 empty] | 0
31 | [7 empty] | 0
32 | [7 empty] | 0
33 | [7 empty] | 0
34 | [7 empty] | 0
35 | [7 empty] | 0
36 | [7 empty] | 0
37 | [7 empty] | 0
38 | [7 empty] | 0
39
40 |  |  | Total Cost of Arch Treatment |  |  |  |  | 0

## 110 Evap Pond
EVAPORATION POND
|  |  |  | (1,000's) | [5 empty] | 110
Project Name: |  | Morichal Power Plant | [6 empty] | Date: | 2010-05-19
Customer: |  | PDVSA | [6 empty] | Quote No: | T 1016-3
Location: |  | Morichal, Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  | "L" | "W" | "D" | Cubic | Cubic | Price | Total
No. |  |  |  | Ft | Ft | Ft | Ft | Yard | cy | Price
1 | Storm Water Evap Pond |  |  | 0 | 0 | 0 | 0 | 0 | 10 | 0
2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
7
8
9
10
11 | [8 empty] | Price
12 | [6 empty] | sf |  | sf
13 | Liner |  |  | 0 | 0 |  | 0 |  | 3 | 0
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36 | [9 empty] | 0

## 200 Buildings
BUILDINGS
[5 empty] | (1,000's) |  |  |  | 200
Project Name: |  | Morichal Power Plant | [5 empty] | Date: | 2010-05-19
Customer: |  | PDVSA | [5 empty] | Quote No: | T 1016-3
Location: |  | Morichal, Venn | [5 empty] | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  | "L" | "W" | SqFt/ | Price | Total
No. |  |  |  |  | Ft | Ft | or Unit | Ft/Unit | Price
1 | Fuel Gas Compressor Shed |  |  |  | 0 | 0 | 0 | 0 | 0
2 | Control/Elect Utility Bldg |  |  |  | 50 | 35 | 1750 | 45 | 78750
3 | Water Treatment |  |  |  | 55 | 40 | 2200 | 40 | 88000
4 | Mech Shed on Utility Bldg |  |  |  | 50 | 35 | 1750 | 30 | 52500
5 | Warehouse/Maintenance |  |  |  | 0 | 0 | 0 | 0 | 0
6 | Substation Bldg |  |  |  | 0 | 0 | 0 | 0 | 0
7 | Steam Turbine Hall |  |  |  | 0 | 0 | 0 | 0 | 0
8 | Liquid Fuel Unloading Shed |  |  |  | 60 | 25 | 1500 | 40 | 60000
9 | Foam Shed |  |  |  | 25 | 20 | 500 | 35 | 17500
10 | Control Room |  |  |  | 0 | 0 | 0 | 0 | 0
11 | Entry Guard House |  |  |  | 0 | 0 | 0 | 0 | 0
12 |  |  |  |  | 0 | 0 | 0 | 0 | 0
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39 |  |  | Total Cost of Other Buildings | [5 empty] | 296.75

## 310, 320, 330 & 340 Mechanical
MECHANICAL EQUIPMENT and Labor
(1,000's)
310 & 330
Project Name: |  | Morichal Power Plant | [9 empty] | Date: |  | 2010-05-19
Customer: |  | PDVSA | [9 empty] | Quote No: |  | T 1016-3
Location: |  | Morichal, Venn | [9 empty] | Est By: |  | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  |  | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
| GTG |  |  | Unit: 3%; Hours: 9
1 | GTG Type LM 6000 PC |  |  | 2 | 0 | 0 | 0 | 0 | 9 | 12 | 30 | 6480 | 52.7387 | 341746.8408
2 | Lube oils and Chemicals |  |  | 2 | 40000 | 80000 | 2400 | 4800 | 9 | 3 | 5 | 270 | 52.7387 | 14239.4517
3 | Exhaust Stack |  |  | 0 | 250000 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
4 | Project Grouting |  |  | 2 | 50000 | 100000 | 3000 | 6000 | 9 | 0 | 0 | 0 | 52.7387 | 0
5 | GTG Tools |  |  | 1 | 50000 | 50000 | 1500 | 1500 | 9 | 0 | 0 | 0 | 52.7387 | 0
6 | Anchor Bolts |  |  | 2 | 60000 | 120000 | 3600 | 7200 | 9 | 0 | 0 | 0 | 52.7387 | 0
7
8 | HRSG
9 | HRSG Type |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
10 | Duct Burner / FD Fan |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
11 | HP BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
12 | LB BFW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
13 | Deaerator |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
14 | ByPass Diverter Valve |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
15
16 | SCR
17 | SCR w/ dilution fan, controls, etc. |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
18 | NH2 Tank w/ pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
19
20 | STG
21 | STG |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
22 | Condenser w/ ejectors |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
23 | Condenser Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
24 | Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
25 | CW Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
26 | Chemical Inj Skid |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
27
28 | Inlet Air Conditioning System
29 | Inlet Chilling Package 4500 Tons Packaged |  |  | 1 | 4700000 | 4700000 | 60000 | 60000 | 9 | 8 | 15 | 1080 | 52.7387 | 56957.8068
30 | Inlet Air Chilled Water GTG Coil |  |  | 1 | 200000 | 200000 | 15000 | 15000 | 9 | 6 | 4 | 216 | 52.7387 | 11391.5614
31 | Inlet Evap Cooling System |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
32 | Inlet Cooling System Cooling Tower |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
33 | Cooling Water Circulation Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
34 | Chilled Water Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
35 | Chemical Inj Skid |  |  | 1 | 15000 | 15000 | 1000 | 1000 | 9 | 3 | 3 | 81 | 52.7387 | 4271.8355
36
37 | Fuel Gas Systems
38 | Fuel Gas compressor w/ Fin Fans |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
39 | Fuel Gas Check KO, Regulator Skid 1200/800 psig |  |  | 1 | 350000 | 350000 | 10500 | 10500 | 9 | 3 | 5 | 135 | 52.7387 | 7119.7258
40 | Fuel Gas Turbine Metering Skid |  |  | 1 | 65000 | 65000 | 1950 | 1950 | 9 | 2 | 2 | 36 | 52.7387 | 1898.5936
41 | Fuel Gas Filter/Reg Skid (500) KW Htr(Htr in Elect) |  |  | 2 | 210000 | 420000 | 12600 | 25200 | 9 | 3 | 4 | 216 | 52.7387 | 11391.5614
42 | ESD Valve, ___" ___# |  |  | 1 | 18000 | 18000 | 540 | 540 | 9 | 2 | 2 | 36 | 52.7387 | 1898.5936
43
44 | Liquid Fuel Systems
45 | Unloading Pump Skid |  |  | 0 | 20000 | 0 | 0 | 0 | 9 | 3 | 3 | 0 | 52.7387 | 0
46 | Metering Skid |  |  | 0 | 90000 | 0 | 0 | 0 | 9 | 3 | 3 | 0 | 52.7387 | 0
47 | Forwarding Pump Skid |  |  | 0 | 20000 | 0 | 0 | 0 | 9 | 3 | 3 | 0 | 52.7387 | 0
48 | Transfer Pump Skid |  |  | 0 | 20000 | 0 | 0 | 0 | 9 | 3 | 3 | 0 | 52.7387 | 0
49 | Fuel Heating |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
50 | Filters |  |  | 0 | 55000 | 0 | 0 | 0 | 9 | 2 | 3 | 0 | 52.7387 | 0
51 | Centrifuge 155,000 GPD |  |  | 0 | 300000 | 0 | 30000 | 0 | 9 | 3 | 6 | 0 | 52.7387 | 0
52 | Injection Pump Skid |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
53 | Storage Tank 450 M CS 3 days |  |  | 0 | 400000 | 0 | 0 | 0 | 9 | 3 | 5 | 0 | 52.7387 | 0
54 | Day Tank 300 M CS coated 2 days |  |  | 0 | 400000 | 0 | 0 | 0 | 9 | 3 | 5 | 0 | 52.7387 | 0
55
56 | Water Supply System
57 | Raw Water Storage Tank M gal |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
58 | Raw Water Supply Pump Skid |  |  | 1 | 25000 | 25000 | 750 | 750 | 9 | 3 | 3 | 81 | 52.7387 | 4271.8355
59 | Raw Water Forwarding Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
60
61 | Water Treatment System
62 | Multi Media Filter Package |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
63 | Water Injection Skid |  |  | 0 |  | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
64 | Demin Treatment System 160 M GPD |  |  | 1 | 550000 | 550000 | 20000 | 20000 | 9 | 4 | 20 | 720 | 52.7387 | 37971.8712
65 | Demin Storage SS Tank gal |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
66 | Demin water fiberglass tank |  |  | 4 | 25000 | 100000 | 3000 | 12000 | 9 | 3 | 5 | 540 | 52.7387 | 28478.9034
67 | Demin forwarding pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
68 | Demin Filter Skid |  |  | 2 | 58000 | 116000 | 3480 | 6960 | 9 | 3 | 2 | 108 | 52.7387 | 5695.7807
69 | RO Tank 21,000 gal |  |  | 1 | 20000 | 20000 | 600 | 600 | 9 | 3 | 2 | 54 | 52.7387 | 2847.8903
70
71 | Waste Water and Oil Storage and Transfer
72 | Oily Water Separator |  |  | 1 | 50000 | 50000 | 2500 | 2500 | 9 | 4 | 5 | 180 | 52.7387 | 9492.9678
73 | Oily Waste Tank 10000 gal |  |  | 1 | 10000 | 10000 | 300 | 300 | 9 | 2 | 2 | 36 | 52.7387 | 1898.5936
74 | Waste Water Tank 10000 gal |  |  | 1 | 10000 | 10000 | 300 | 300 | 9 | 2 | 2 | 36 | 52.7387 | 1898.5936
75 | Waste Oil and Water forwarding pumps w/ skid |  |  | 2 | 8000 | 16000 | 480 | 960 | 9 | 2 | 3 | 108 | 52.7387 | 5695.7807
76
77 | Fire Control Systems
78 | Fire Water Foam System |  |  | 1 | 150000 | 150000 | 4500 | 4500 | 9 | 4 | 5 | 180 | 52.7387 | 9492.9678
79 | Fire Water System, valves, hydrants, monitors |  |  | 1 | 200000 | 200000 | 6000 | 6000 | 9 | 0 | 0 | 0 | 52.7387 | 0
80
81 | Storm Water System
82 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
83 | HDPE Pipe - (__)" |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
84 | Sump Pumps |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
85
86 | Other Systems
87 | Instrument Air Compressor Package, net (___) scfm |  |  | 1 | 75000 | 75000 | 2250 | 2250 | 9 | 3 | 4 | 108 | 52.7387 | 5695.7807
88 | Potable Water System |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
89 | Anti-Icing Ducting |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
90 | Sanitary Sewer |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
91 |  |  |  | Hours: 9
92
93 |  |  | Total Cost | Total: 7440; Frt: 190.81; Qty: 10701
94 |  |  |  | Total: 564.3569
[9 empty] | Total Manhours |  |  | 10701
[9 empty] | Times Prod Factor |  | 1.5 | 16051.5 | 52.7387 | 846.5354
95 | BOP Pipe, Valves and Fittings Labor |  |  | 1 | 250000 | 250000 | 7500 | 7500 | 9 | 8 | 150 | 10800 | 52.7387 | 569578.068
96 |  |  | Total Cost | Total: 250; Frt: 7.5; Qty: 10800; Total: 569578.068
97
98 |  |  |  | Hours: Total Manhours; Qty: 10800
99 |  |  |  | Hours: Times Prod Factor; Qty: 1.5; Qty: 16200; Rate: 52.7387; Total: 854.3671
Price per hour based with all labor burdens as follows:
[8 empty] | Local Hrly Cost |  | 27
[8 empty] | Fringes |  | 2.5
[8 empty] | Small Tools |  | 1.5
[8 empty] | Labor Burden 35% |  | 9.45
40.45
[8 empty] | Contr G&A 8% |  | 3.236
[8 empty] | Contr Mark up 15% |  | 6.0675
49.7535
[7 empty] | 45 | Hour Work Week = |  | 52.7387
Work Week Hours Multiplier
[7 empty] | 45 | 50 | 60
[7 empty] | 1.06 | 1.1 | 1.17
Note on K127: Insert Weekly M/hrs Here: Weekly M/hrs automatically calculated hrs/day.
Note on N119: Insert Rate Here:

## 410, 430, 450 & 460 Electrical
ELECTRICAL EQUIPMENT and Labor
(1,000's)
410, 430, 450 & 460
Project Name: |  | Morichal Power Plant | [11 empty] | Date: |  | 2010-05-19
Customer: |  | PDVSA | [11 empty] | Quote No: |  | T 1016-3
Location: |  | Morichal, Venn | [11 empty] | Est By: |  | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  | Mfgr. | Location | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. | [6 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 | Power Island Equipment | [7 empty] | 3% |  | 9
2 | Gas Turbine Generator |  |  |  |  | 2 |  |  | 0 |  | 9 | 8 | 30 | 4320 | 52.7387 | 227831.2272
3 | HRSG |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 52.7387 | 0
4 | SCR |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 52.7387 | 0
5 | STG |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 52.7387 | 0
6 | STG Cooling Tower |  |  |  |  | 0 |  |  | 0 |  | 9 | 0 | 0 | 0 | 52.7387 | 0
7 | Chiller Package |  |  |  |  | 1 |  |  | 0 |  | 9 | 6 | 20 | 1080 | 52.7387 | 56957.8068
8 | Water Treatment Package |  |  |  |  | 1 |  |  | 0 |  | 9 | 4 | 15 | 540 | 52.7387 | 28478.9034
9 | [13 empty] | 0 | 52.7387 | 0
10 | 15KV | [13 empty] | 52.7387
11 | Generator Breaker(s) |  |  |  |  | 2 | 135000 | 270000 | 8100 | 16200 | 9 | 4 | 5 | 360 | 52.7387 | 18985.9356
12 | Distribution Breaker(s) |  |  |  |  | 4 | 70000 | 280000 | 8400 | 33600 | 9 | 4 | 4 | 576 | 52.7387 | 30377.497
13 | Fused Disconnect(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 3 | 4 | 0 | 52.7387 | 0
14 | Cable Bus |  |  |  |  | 2 | 125000 | 250000 | 7500 | 15000 | 9 | 3 | 4 | 216 | 52.7387 | 11391.5614
15 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 4 | 0 | 52.7387 | 0
16 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 6 | 0 | 52.7387 | 0
17 | 5KV | [13 empty] | 52.7387
18 | Distribution Breaker(s) |  |  |  |  | 0 | 55000 | 0 | 1000 | 0 | 9 | 2 | 3 | 0 | 52.7387 | 0
19 | Fused Disconnect(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 6 | 0 | 52.7387 | 0
20 | MCC's |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | 0 | 52.7387 | 0
21 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 6 | 0 | 52.7387 | 0
22 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 52.7387 | 0
23 | 600V | [13 empty] | 52.7387
24 | Distribution Panel(s) |  |  |  |  | 1 | 180000 | 180000 | 2500 | 2500 | 9 | 2 | 5 | 90 | 52.7387 | 4746.4839
25 | GTG MCC(s) |  |  |  |  | 2 | 50000 | 100000 | 3000 | 6000 | 9 | 2 | 5 | 180 | 52.7387 | 9492.9678
26 | HRSG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 4 | 0 | 52.7387 | 0
27 | STG MCC(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 52.7387 | 0
28 | BOP MCC(s) |  |  |  |  | 1 | 15000 | 15000 | 450 | 450 | 9 | 2 | 3 | 54 | 52.7387 | 2847.8903
29 | Water Treatment MCC(s) |  |  |  |  | 1 | 15000 | 15000 | 450 | 450 | 9 | 2 | 2 | 36 | 52.7387 | 1898.5936
30 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 8 | 0 | 52.7387 | 0
31 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 52.7387 | 0
32 | Aux Transformer(s) | [13 empty] | 52.7387
33 | 15/5KV _2.5__ MVA |  |  |  |  | 1 | 105000 | 105000 | 5000 | 5000 | 9 | 3 | 5 | 135 | 52.7387 | 7119.7258
34 | 15/600V __500____ KVA |  |  |  |  | 3 | 50000 | 150000 | 4000 | 12000 | 9 | 3 | 5 | 405 | 52.7387 | 21359.1776
35 | 600/120/208V ________ KVA |  |  |  |  | 1 | 5000 | 5000 | 150 | 150 | 9 | 3 | 3 | 81 | 52.7387 | 4271.8355
36 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
37 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
38 | Area Lighting | [13 empty] | 52.7387
39 | Poles _______ High |  |  |  |  | 5 | 2000 | 10000 | 300 | 1500 | 9 | 2 | 1 | 90 | 52.7387 | 4746.4839
40 | Floodlights _______ Watts |  |  |  |  | 10 | 500 | 5000 | 50 | 500 | 9 | 2 | 0.2 | 36 | 52.7387 | 1898.5936
41 | [5 empty] | 0 | 0 | 0 |  | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
42 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 60 | 0 | 52.7387 | 0
43 | Other Systems | [13 empty] | 52.7387
44 | UPS |  |  |  |  | 1 | 5000 | 5000 | 150 | 150 | 9 | 2 | 3 | 54 | 52.7387 | 2847.8903
45 | DC |  |  |  |  | 1 | 20000 | 20000 | 5000 | 5000 | 9 | 2 | 3 | 54 | 52.7387 | 2847.8903
46 | Cathodic Protection |  |  |  |  | 2 | 15000 | 30000 | 900 | 1800 | 9 | 4 | 4 | 288 | 52.7387 | 15188.7485
47 | Lightning Protection |  |  |  |  | 2 | 12000 | 24000 | 720 | 1440 | 9 | 4 | 4 | 288 | 52.7387 | 15188.7485
48 | [11 empty] | 0 | 0 | 0 | 52.7387 | 0
49 | [14 empty] | 52.7387
50 | Temporary Electric |  |  |  |  | 1 | 25000 | 25000 | 750 | 750 | 9 | 2 | 35 | 630 | 52.7387 | 33225.3873
51 | Electrical Control Module |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
52 | [6 empty] | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
53 | [6 empty] | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
54 | [6 empty] | 0 | 0 |  | 0 | 9 | 0 | 0 | 0 | 52.7387 | 0
55 |  |  | Total Cost of Electrical Equipment |  |  |  |  | 1489 |  | 102.49 |  |  |  | 9513 |  | 501.7033
[12 empty] | Productivity | 1.5 | 14269.5 | 52.7387 | 752.555
56 | Cable Tray, Conduit, & Cable |  |  |  |  | 1 | 600000 | 600000 | 18000 | 18000 | 9 | 8 | 150 | 10800 | 52.7387 | 569578.068
57 |  |  | Total Cost of Electrical Equipment |  |  |  |  | 600 |  | 18 |  |  |  | 10800 |  | 569.5781
58 | [10 empty] | Total Manhours |  |  | 10800
59 | [10 empty] | Times Prod Factor |  | 1.5 | 16200 | 52.7387 | 854.3671
Price per hour based with all labor burdens as follows:
[13 empty] | Local Hrly Cost |  | 27
[13 empty] | Fringes |  | 2.5
[13 empty] | Small Tools |  | 1.5
[13 empty] | Labor Burden 35% |  | 9.45
40.45
[13 empty] | Contr G&A 8% |  | 3.236
[13 empty] | Contr Mark up 15% |  | 6.0675
49.7535
[12 empty] | 45 | Hour Work Week = |  | 52.7387
Work Week Hours Multiplier
[12 empty] | 45 | 50 | 60
[12 empty] | 1.06 | 1.1 | 1.17
Note on N87: Insert Weekly M/hrs Here: Automatically calculates hrs/day.
Note on Q79: Insert Rate Here:

## 420 & 440 Substation
SUBSTATION EQUIPMENT and Labor
(1,000's)
Project Name: |  | Morichal Power Plant | [12 empty] | Date: | 2010-05-19
Customer: |  | PDVSA | [12 empty] | Quote No: | T 1016-3
Location: |  | Morichal, Venn | [12 empty] | Est By:
Bid Due Date: |  | 2010-05-20
Item |  | Description |  | Mfgr | Loc | Qty | Unit | Total | Unit | Frt | Hours | Qty | Qty | Qty | Rate | Total
No. | [6 empty] | Price | Price | Frt Pr | Price | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 |  |  |  | Unit: 3%; Hours: 9
2 | Main Power Transformer 13.8/34 KV, _60_ MVA |  |  |  |  | 2 | 0 | 0 | 0 | 0 | 9 | 4 | 10 | 720 | 52.7387 | 37971.8712
3 | SF6 Circuit Breaker(s) _34_ KV |  |  |  |  | 2 | 50000 | 100000 | 3000 | 6000 | 9 | 2 | 6 | 216 | 52.7387 | 11391.5614
4 | Disconnect Switches ______ KV |  |  |  |  | 3 | 20000 | 60000 | 1800 | 5400 | 9 | 2 | 4 | 216 | 52.7387 | 11391.5614
5 | Station Post Insulators ____ KV |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 0.05 | 0 | 52.7387 | 0
6 | Insulator Stanchons ______ High |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.5 | 0 | 52.7387 | 0
7 | Insulator Stanchons ______ High |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.4 | 0 | 52.7387 | 0
8 | Dead End Tower(s) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 5 | 0 | 52.7387 | 0
9 | One Lot revise existing pipe bus |  |  |  |  | 1 | 75000 | 75000 | 2250 | 2250 | 9 | 3 | 8 | 216 | 52.7387 | 11391.5614
10 | Alum Bus Conn's |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.1 | 0 | 52.7387 | 0
11 | Alum Bus End Plugs _____ Dia |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.05 | 0 | 52.7387 | 0
12 | Alum Bus Support Clamps |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.1 | 0 | 52.7387 | 0
13 | Alum Bus "V" Conn's |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.08 | 0 | 52.7387 | 0
14 | Static Wire Poles, ____ High |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 1 | 0 | 52.7387 | 0
15 | Area Lighting Poles, ____ High |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 1 | 0 | 52.7387 | 0
16 | Flood Lights, ______ Watts |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 52.7387 | 0
17 | #4/0 Grounding Conductor |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 0.03 | 0 | 52.7387 | 0
18 | 3/4"x10'-0" Ground Rods & Clamps |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0.04 | 0 | 52.7387 | 0
19 | #90 Cadweld Shots |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 0.3 | 0 | 52.7387 | 0
20 | Metering CT's & CPT's |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 52.7387 | 0 | 0
21 | Station Metering w/ In & Out Capabilities |  |  |  |  | 1 | 35000 | 35000 | 1050 | 1050 | 9 | 2 | 5 | 90 | 52.7387 | 4746.4839
22 | Station Protective Relay(s) |  |  |  |  | 1 | 55000 | 55000 | 1650 | 1650 | 9 | 2 | 5 | 90 | 52.7387 | 4746.4839
23 | Station RTU |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 5 | 0 | 52.7387 | 0
24 | 125V DC System |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 52.7387 | 0
25 | Transmission Line Poles |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 2 | 0 | 52.7387 | 0
26 | Transmission Line Strain Insulators |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0 | 0 | 52.7387 | 0 | 0
27 | Cable Bus, Type _____, Size _____ |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 6 | 0 | 52.7387 | 0
28 | Main Power Transformer Oil, ______ Gal |  |  |  |  | 2 | 45000 | 90000 | 2700 | 5400 | 9 | 2 | 5 | 180 | 52.7387 | 9492.9678
29 | Main Power Transformer Dress Out & Test |  |  |  |  | 2 | 50000 | 100000 | 3000 | 6000 | 9 | 2 | 0 | 0 | 52.7387 | 0
30 | Fiber Optic Cable w/ Messenger Cable |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 5 | 0 | 52.7387 | 0 | 0
31 | Fiber Optic Cable Fittings & Terminations |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 2 | 0 | 52.7387 | 0
32 |  |  |  | Hours: 9; Rate: 52.7387
33 |  |  |  | Hours: 9; Rate: 52.7387
34 |  |  |  | Hours: 9; Rate: 52.7387
35 |  |  |  | Hours: 9; Rate: 52.7387; Total: 0
36 |  |  | Total Cost of Substation Equipment | Total: 515; Frt: 27.75; Qty: 1728; Total: 91.1325
[12 empty] | Total Hours |  | 1728
[12 empty] | Prod Factor | 1.5 | 2592 | 52.7387 | 136.6987
Price per hour based with all labor burdens as follows:
[13 empty] | Local Hrly Cost |  | 27
[13 empty] | Fringes |  | 2.5
[13 empty] | Small Tools |  | 1.5
[13 empty] | Labor Burden 35% |  | 9.45
40.45
[13 empty] | Contr G&A 8% |  | 3.236
[13 empty] | Contr Mark up 15% |  | 6.0675
49.7535
[12 empty] | 45 | Hour Work Week = |  | 52.7387
Work Week Hours Multiplier
[12 empty] | 45 | 50 | 60
[12 empty] | 1.06 | 1.1 | 1.17
Note on N61: Insert Weekly M/hrs Here: Automatically calculates hrs/day.
Note on Q53: Insert Rate Here:

## 510 CEMS
CEM's
[5 empty] | (1,000's) |  |  | 510
Project Name: |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Cems | Cost | Cost
1
2 | Rosemont CEM's Unit Most States for 1 ea GTG |  |  |  |  | 0 | 120000 | 0
3
4 | Rosemont CEM's Unit for Califormia for 1 ea GTG |  |  |  |  | 0 | 130000 | 0
5
6 | Installation Support |  |  |  |  | 0 | 18000 | 0
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39 |  |  | Total Cost of CEM's |  |  |  |  | 0

## 520 & 530 Instrumentation
PLANT INSTRUMENTATION
(1,000's)
520 &530
Project Name: |  | Morichal Power Plant | [8 empty] | Date: | 2010-05-19
Customer: |  | PDVSA | [8 empty] | Quote No: | T 1016-3
Location: |  | Morichal, Venn | [8 empty] | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  | Qty | Unit | Total | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  | GTG's | Cost | Cost | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 |  |  |  | Hours: 9
2 | Instrumentation for GTG |  |  | 2 | 25000 | 50000 | 9 | 2 | 10 | 360 | 40.4178 | 14550.408
3 |  |  |  | Hours: 9; Rate: 40.4178; Total: 0
4 | Instrumentation for Chiller |  |  | 1 | 35000 | 35000 | 9 | 4 | 15 | 540 | 40.4178 | 21825.612
5 |  |  |  | Hours: 9; Rate: 40.4178
6 | Instrumentation for HRSG |  |  | 0 | 0 | 0 | 9 | 4 | 15 | 0 | 40.4178 | 0
7 |  |  |  | Hours: 9; Rate: 40.4178
8 | Instrumentation for Injection Water Treatment |  |  | 1 | 20000 | 20000 | 9 | 2 | 10 | 180 | 40.4178 | 7275.204
9 |  |  |  | Hours: 9; Rate: 40.4178
10 | Instrumentation for Diesel Fuel Treatment |  |  | 1 | 20000 | 20000 | 9 | 2 | 10 | 180 | 40.4178 | 7275.204
11 |  |  |  | Hours: 9; Rate: 40.4178
12 | Instrumentation for gas compressors |  |  | 0 | 0 | 0 | 9 | 4 | 5 | 0 | 40.4178 | 0
13 |  |  |  | Hours: 9; Rate: 40.4178
14 | Labor to Install CEMS |  |  | 0 | 0 | 0 | 9 | 4 | 5 | 0 | 40.4178 | 0
15 |  |  |  | Hours: 9; Rate: 40.4178
16 |  |  |  | Hours: 9; Rate: 40.4178
17 |  |  |  | Hours: 9; Rate: 40.4178
18 |  |  |  | Hours: 9; Rate: 40.4178
19 |  |  |  | Hours: 9; Rate: 40.4178
20 |  |  |  | Hours: 9; Rate: 40.4178
21 |  |  |  | Hours: 9; Rate: 40.4178
22 |  |  |  | Hours: 9; Rate: 40.4178
23 |  |  | Total Cost of Plant Instrumentation | Total: 125; Qty: 1260; Total: 50.9264
[8 empty] | Total Hours |  | 1260
[8 empty] | Prod Factor | 1.5 | 1890 | 40.4178 | 76.3896
Price per hour based with all labor burdens as follows:
[9 empty] | Local Hrly Cost |  | 20
[9 empty] | Fringes |  | 2.5
[9 empty] | Small Tools |  | 1.5
[9 empty] | Labor Burden 35% |  | 7
31
[9 empty] | Contr G&A 8% |  | 2.48
[9 empty] | Contr Mark up 15% |  | 4.65
38.13
[8 empty] | 45 | Hour Work Week = |  | 40.4178
Work Week Hours Multiplier
[8 empty] | 45 | 50 | 60
[8 empty] | 1.06 | 1.1 | 1.17
Note on L50: Insert Weekly M/hrs Here: Automatically calculates hr/day.
Note on O42: Inset Rate Here:

## 610, 620, 630 & 640 DCS
DCS
|  |  |  | (1,000's) |  |  |  | 610, 620, 630 & 640
Project Name: |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [6 empty] | Cost | Cost
1
2 | DCS Hardware / Software |  |  |  |  | 1 | 325000 | 325000
3
4 | Lot of Misc interconnecting cables etc. |  |  |  |  | 1 | 15000 | 15000
5
6 | Documentation |  |  |  |  | 1 | 75000 | 75000
7
8 |  |  |  |  | Total DCS |  |  | 415
9
10 | PBX Communications System |  |  |  |  | 1 | 20000 | 20
11
12 | Loud Speaker System |  |  |  |  | 1 | 20000 | 20
13
14 | TV / Security System |  |  |  |  | 0 | 20000 | 0
15
16
17
[7 empty] | taxable | 340040

## 700 Erection
PLANT ERECTION
(1,000's)
700
Project Name: |  | Morichal Power Plant | [6 empty] | Date: | 2010-05-19
Customer: |  | PDVSA | [6 empty] | Quote No: | T 1016-3
Location: |  | Morichal, Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  | No | Hours | Qty | Qty | Qty | Rate | Total
No. |  |  |  | Units | (day) | (men) | (days) | (mhrs) | (hour) | Labor
1 |  |  |  |  | 9
2 | GTG Erection |  |  | 2 | 9 | 12 | 30 | 6480 | 52.7387 | 341746.8408
3 |  |  |  |  | 9 |  |  |  | 52.7387
4 | HRSG Erection |  |  | 0 | 9 | 10 | 60 | 0 | 52.7387 | 0
5 |  |  |  |  | 9 |  |  |  | 52.7387
6 | Chiller Erection |  |  | 1 | 9 | 8 | 15 | 1080 | 52.7387 | 56957.8068
7 |  |  |  |  | 9 |  |  |  | 52.7387
8 | Water Treatment and FW Systems |  |  | 1 | 9 | 6 | 15 | 810 | 52.7387 | 42718.3551
9 |  |  |  |  | 9 |  |  |  | 52.7387
10 | Liquid Fuel Treatment System |  |  | 0 | 9 | 4 | 5 | 0 | 52.7387 | 0
11 |  |  |  |  | 9 |  |  |  | 52.7387
12 | BOP Equip Erection |  |  | 0 | 9 | 6 | 10 | 0 | 52.7387 | 0
13 |  |  |  |  | 9 |  |  |  | 52.7387
14 | Gas Compressor Erection |  |  | 0 | 9 | 6 | 5 | 0 | 52.7387 | 0
15 |  |  |  |  | 9 |  |  |  | 52.7387
16 | Evap Cooling Erection |  |  | 0 | 9 | 4 | 4 | 0 | 52.7387 | 0
17 |  |  |  |  | 9 |  |  |  | 52.7387
18 | Fire Water Pump Skid |  |  | 0 | 9 | 4 | 3 | 0 | 52.7387 | 0
19 |  |  |  |  | 9 |  |  |  | 52.7387
20 | STG Erection |  |  | 0 | 9 | 12 | 36 | 0 | 52.7387 | 0
21 |  |  |  |  | 9 |  |  |  | 52.7387
22 | STG Cooling Tower |  |  | 0 | 9 | 8 | 8 | 0 | 52.7387 | 0
23 |  |  |  |  | 9 |  |  |  | 52.7387
24 |  |  |  |  | 9 |  |  |  | 52.7387
25 |  |  | Total Cost of Plant Erection |  |  |  |  | 8370 |  | 441.423
[6 empty] | Total Hours |  | 8370
[6 empty] | Prod Factor | 1.5 | 12555 | 52.7387 | 662.1345
Price per hour based with all labor burdens as follows:
[7 empty] | Local Hrly Cost |  | 27
[7 empty] | Fringes |  | 2.5
[7 empty] | Small Tools |  | 1.5
[7 empty] | Labor Burden 35% |  | 9.45
40.45
[7 empty] | Contr G&A 8% |  | 3.236
[7 empty] | Contr Mark up 15% |  | 6.0675
49.7535
[6 empty] | 45 | Hour Work Week = |  | 52.7387
Work Week Hours Multiplier
[6 empty] | 45 | 50 | 60
[6 empty] | 1.06 | 1.1 | 1.17
Note on J52: Insert Weekly M/hrs Here: Automatically calculates hr/day.
Note on M44: Insert Rate Here:

## 800 Equip rent
EQUIPMENT RENTAL
[5 empty] | (1,000's) |  |  |  |  | 800
Project Name: |  | Morichal Power Plant | [6 empty] | Date: | 2010-05-19
Customer: |  | PDVSA | [6 empty] | Quote No: | T 1016-3
Location: |  | Morichal, Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | No. | Days | Total | Cost | Total
No. | [5 empty] | Units | Unit | Days | Per Day | Cost
1 | GTG Equip Rental per ea GTG
2 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 2 | 10 | 20 | 6000 | 120000
3 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
4 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 2 | 120 | 240 | 2000 | 480000
5 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
6 | 2 ea Sky Tracs |  |  |  |  | 2 | 45 | 90 | 70 | 6300
7 | 2 ea Fork Lifts |  |  |  |  | 1 | 45 | 45 | 70 | 3150
8 | 1 ea Man Lift |  |  |  |  | 0 | 0 | 0 | 80 | 0
9 | 2 ea Welders |  |  |  |  | 2 | 45 | 90 | 60 | 5400
10
11 | HRSG Erection
12 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
13 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
14 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
15 | 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
16 | 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
17 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
18 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
19
20 | SCR/CO
21 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
22 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
23 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
24 | 1 ea 40 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
25 | 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
26 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
27 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
28
29 | STG
30 | 1 ea 200 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
31 | 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
32 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1000 | 0
33 | 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
34 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
35 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
36
37 | Chiller Package w/ Cooling Tower
38 | 150 Ton Crane |  |  |  |  | 1 | 8 | 8 | 4000 | 32000
39 | 40 Ton Crane |  |  |  |  | 1 | 20 | 20 | 2000 | 40000
40 | 2ea Fork Lifts |  |  |  |  | 0 | 0 | 0 | 70 | 0
41
42 | Fuel Gas Compressor Rental per Compr Skid
43 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
44 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 1500 | 0
45
46 | BOP Equip Rental per ea GTG
47 | 1 ea 300 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 4000 | 0
48 | 1 ea 150 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3000 | 0
49 | 1 ea 50 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 2000 | 0
50 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 150 | 150 | 2000 | 300000
51 | 2 ea Fork Lifts |  |  |  |  | 1 | 150 | 150 | 70 | 10500
52 | 2 ea Sky Tracs |  |  |  |  | 2 | 150 | 300 | 70 | 21000
53 | 2 ea Pick ups |  |  |  |  | 0 | 0 | 0 | 30 | 0
54 | 1 ea Front End Loader / Back Hoe |  |  |  |  | 1 | 150 | 150 | 70 | 10500
55
56 | Substation Equip Rental
57 | 1 ea 200 Ton Crane w/ operator |  |  |  |  | 2 | 5 | 10 | 4000 | 40000
58 | 1 ea 100 Ton Crane w/ operator |  |  |  |  | 0 | 0 | 0 | 3500 | 0
59 | 1 ea 20 Ton Crane w/ operator |  |  |  |  | 1 | 45 | 45 | 1500 | 67500
60 | 2 ea Man Lifts |  |  |  |  | 0 | 0 | 0 | 80 | 0
61 | 2 ea Sky Tracs |  |  |  |  | 0 | 0 | 0 | 70 | 0
62 | 5 ea Welders |  |  |  |  | 0 | 0 | 0 | 80 | 0
63
64
65
66
67
68 |  |  | Total Cost of Plant Equip Rental |  |  |  |  | 1318 |  | 1136.35

## 900 Paint
PLANT PAINTING
[5 empty] | (1,000's) |  |  | 900
Project Name: |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Paint for GTG |  |  |  |  | 2 | 60000 | 120000
3
4 | Paint for STG and Auxiliaries |  |  |  |  | 0 | 60000 | 0
5
6 | Paint for SCR w/ Pipe Racks |  |  |  |  | 0 | 135000 | 0
7
8 | Paint for Pipe Rack etc. |  |  |  |  | 1 | 40000 | 40000
9
10 | Paint for BOP Equipment |  |  |  |  | 1 | 65000 | 65000
11
12 | Paint for Gas Compressor |  |  |  |  | 0 | 15000 | 0
13
14 | Paint for Water Treatment |  |  |  |  | 1 | 15000 | 15000
15
16 | Paint for Waste Water Treatment |  |  |  |  | 0 | 15000 | 0
17
18 | Paint for HRSG |  |  |  |  | 0 | 95000 | 0
19
20
21
22
23
24
25
26
27
28
29
30 |  |  | Total Cost of Plant Painting |  |  |  |  | 240

## 1000 Transportation
PLANT TRANSPORTATION
[5 empty] | (1,000's) |  |  | 1000
Project Name: |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Transportation of Plant Major Mechanical Equip |  |  |  |  | 1 | 190.81 | 190.81
3
4 | Transportation of Plant Major Electrical Equip |  |  |  |  | 1 | 102.49 | 102.49
5
6 | Transportation Substation Equip |  |  |  |  | 1 | 27.75 | 27.75
7
8 | Transportation of GTG
9
10 | Transportation of SCR
11
12 | Transportation of HRSG
13
14 | Transportation of STG
15
16 | Pipe, Valves & Fittings |  |  |  |  | 1 | 7.5 | 7.5
17
18 | Conduit, Cable & Wire |  |  |  |  | 1 | 18 | 18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Plant Transportation |  |  |  |  | 346.55

## 1100 Site Costs
SITE COSTS
[5 empty] | (1,000's) |  |  |  |  | 1100
Project Name: |  | Morichal Power Plant | [6 empty] | Date: | 2010-05-19
Customer: |  | PDVSA | [6 empty] | Quote No: | T 1016-3
Location: |  | Morichal, Venn | [6 empty] | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | No. | No. | Cost | Total | Total
No. | [5 empty] | Units | Mos | Per Mo | Mo Cost | Cost
1 | Monthly Site Costs
2 | Office Trailers |  |  |  |  | 4 | 7 | 1500 | 42000
3 | Porta Potties |  |  |  |  | 4 | 7 | 300 | 8400
4 | Water and Ice |  |  |  |  | 1 | 7 | 500 | 3500
5 | Fed X |  |  |  |  | 1 | 7 | 300 | 2100
6 | Telephone |  |  |  |  | 1 | 7 | 2500 | 17500
7 | Office Supplies |  |  |  |  | 1 | 7 | 1000 | 7000
8 | [6 empty] | 7
9 | Diesel Fuel for Power Generator and Welders |  |  |  |  | 1 | 7 | 3000 | 21000
10 | Misc Items |  |  |  |  | 1 | 7 | 3000 | 21000
11 |  |  | Total Monthly Cost | [5 empty] | 122500
12
13
14
15
16
17
18 | Monthly Site Costs | [5 empty] | 1 | 122500 |  | 122500
19 | One Time Costs
20 | 500 KW Diesel Generator w/ Dist Equip | [8 empty] | 200000
21 | Cad Station | [8 empty] | 10000
22 | Computers | [8 empty] | 5000
23 | Telephone System and Satalite Dish | [8 empty] | 15000
24 | Plotter | [8 empty] | 0
25 | Fax Machine and Printers | [8 empty] | 3000
26 | Misc equip | [8 empty] | 5000
27 | Signs | [8 empty] | 0
28
29
30
31
32 | Total Project Cost = Cost per Month Times Number of Mos
33 | Plus the Project One Time Costs.
34
35 |  |  | Total Cost of Project Site Costs | [6 empty] | 360.5

## 1200 Engineering
ENGINEERING
[5 empty] | (1,000's) |  |  | 1200
Project Name: |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Conceptual Engineering PES |  |  |  |  | 1 | 25000 | 25000
3
4 | Detailed Engineering per GTG |  |  |  |  | 2 | 300000 | 600000
5
6 | Detailed Engineering per HRSG |  |  |  |  | 0 | 0 | 0
7
8 | Detailed Engineering per STG |  |  |  |  | 0 | 0 | 0
9
10 | Detailed Engineering per Gas Compressor |  |  |  |  | 0 | 0 | 0
11
12 | Detailed Engineering per Water Treatment |  |  |  |  | 1 | 20000 | 20000
13
14 | Detailed Engineering for Civil / Structural Steel |  |  |  |  | 1 | 75000 | 75000
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33 |  |  | Total Cost of Engineering |  |  |  |  | 720

## 1210 Local Engineering
LOCAL ENGINEERING
[5 empty] | (1,000's) |  |  | 1210
Project Name: |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | Qty | Unit | Total
No. | [5 empty] | Units | Cost | Cost
1
2 | Soils & Environmental Eng |  |  |  |  | 1 | 25000 | 25000
3
4 | Civil Engineer |  |  |  |  | 4 | 25000 | 100000
5
6 | Mechanical Engineer |  |  |  |  | 4 | 25000 | 100000
7
8 | Electrical Engineer |  |  |  |  | 4 | 25000 | 100000
9
10 | Other |  |  |  |  | 0 | 0 | 0
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40 |  |  | Total Cost of Local Engineering |  |  |  |  | 325

## 1310 & 1320 PM-CM-Insp
PROJECT MANAGEMENT LABOR
|  |  |  | (1,000's) |  |  |  | 1310 & 1320
Project Name: |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | No. | Cost | Total
No. | [5 empty] | Mos | Per Mo | Cost
Home Office
1 | Project Mgr Months on Project |  |  |  |  | 7 | 16000 | 112000
2 | Admin Mgr Months on Project |  |  |  |  | 6 | 10000 | 60000
3 | Scheduler |  |  |  |  | 3 | 8000 | 24000
4 | Purchasing Agent |  |  |  |  | 2 | 8000 | 16000
5 | Expediter |  |  |  |  | 0 | 5000 | 0
6 | Home Office Logistic Coordinator |  |  |  |  | 0 | 9000 | 0
7
8
9 | [6 empty] | 212000
10
11
12
13
14
15
16 | Site Construction
17 | Secretary |  |  |  |  | 8 | 4000 | 32000
18 | Construction Mngr |  |  |  |  | 8 | 18000 | 144000
19 | Contract Cost Admin |  |  |  |  | 0 | 10000 | 0
20 | Scheduler |  |  |  |  | 3 | 8000 | 24000
21 | Mechanical Supervisor |  |  |  |  | 6 | 15000 | 90000
22 | Electrical Supervisor |  |  |  |  | 6 | 15000 | 90000
23 | Civil Supervisor |  |  |  |  | 4 | 15000 | 60000
24 | Clerks |  |  |  |  | 8 | 5000 | 40000
25 | Warehousemen |  |  |  |  | 8 | 3000 | 24000
26 | Draftsman |  |  |  |  | 4 | 6000 | 24000
27 | Security |  |  |  |  | 7 | 12000 | 84000
28 | Safety |  |  |  |  | 6 | 9000 | 54000
29 | QA/QC Mngr |  |  |  |  | 6 | 9000 | 54000
30
31
32 | [6 empty] | 720000
33
34 | Commissioning Techs __ ea __ mos x __ |  |  |  |  | 8 | 12000 | 96000
35
36
37
38 | Training |  |  |  |  | 0 | 0 | 0
39
40 |  |  |  |  | Total Project & Construction Management |  |  | 1028
41
42
43
44
45 | Inspectors
46 | Civil - Structual __ ea ___ mos |  |  |  |  | 0 | 11500 | 0
47 | Mechanical __ ea ___ mos |  |  |  |  | 0 | 11500 | 0
48 | Electrical __ ea ___ mos |  |  |  |  | 0 | 11500 | 0
49 | Welder __ ea ___ mos | __ ea ___ mos |  |  |  | 0 | 11500 | 0
50
51 |  |  |  |  | Total Inspectors |  |  | 0
52

## 1400 & 1410 Travel & Perdiem
PROJECT MGT TVL AND PER DIEM
|  |  |  | (1,000's) |  |  |  | 1400 & 1410
Project Name: |  | Morichal Power Plant |  |  |  |  | Date: | 2010-05-19
Customer: |  | PDVSA |  |  |  |  | Quote No: | T 1016-3
Location: |  | Morichal, Venn |  |  |  |  | Est By: | WTS
Bid Due Date: |  | 2010-05-20
Item |  | Description |  |  |  | No. | Cost | Total
No. | [5 empty] | Units | Per Unit | Cost
1
2 | Project & Construciton Management
3 | R T Air Fares |  |  |  |  | 40 | 2700 | 108000
4 | Months of Per Diem at Site (Mgt) |  | Assumes Apartment Rental, meals, etc. |  |  | 28 | 3000 | 84000
5 | Number of Months of Pick Up Trucks |  |  |  |  | 25 | 3000 | 75000
6 | Misc expenditures |  |  |  |  | 1 | 50000 | 50000
7 | Days Per Diem - Lodging & Meals (Techs) |  |  |  |  | 700 | 52 | 36400
8
9
10
11
12
13 | Engineering
14 | Round Trip Air Fare for Eng Visits to site |  |  |  |  | 6 | 2700 | 16200
15 | Days of Per Diem Cost for Eng Days at Site |  |  |  |  | 120 | 250 | 30000
16 | Auto Rental for Eng Days at Site |  |  |  |  | 0 | 0 | 0
17 | Misc Travel Expentitures |  |  |  |  | 0 | 0 | 0
18
19
20 |  |  |  |  | Total Cost of Project Mgt Tvl and Per Diem |  |  | 399.6
21
22
23
24 | Engineering Meal Expense |  |  |  |  | 0 | 50 | 0 | 0
25
26 | Project Mgt Meal Expense |  |  |  |  | 0 | 50 | 0 | 0
27
28 |  |  |  |  | Total Meal Expense |  |  | 0
29
30
31
32
33
34
35
36