PROPOSAL

Presented To:

CORPOELEC

For

1 x Rolls-Royce Trent 60

Turbine Equipment

Prepared By

Proposal No. 710-3131

March 17, 2010

This document is privileged and contains confidential information intended for use only by

MDE

Introduction

JTURBINES (“JT”) is pleased to provide this proposal to Ministerio de La Electricidad (“Corpoelec”) for One (1) Brand New Rolls-Royce Trent 60 Gas Turbines.

Trent 60 WLE Power Generation Package

Scope of Supply

JTURBINES offers the delivery of One (1) Brand New Rolls-Royce Trent 60 Wet Low Emissions (WLE) Gas Turbine Power Generation Packages, designed in accordance with the specifications outlined in this proposal, comprising of:

### Gas Turbine

#### Trent 60 WLE

- Rolls-Royce Industrial Trent 60 Gas Turbine WLE, Dual Fuel

- On engine mounted lubrication pump and hydraulic starter

- Gas Turbine ignition system consisting of sixteen on-engine igniters with seals, eight on-engine high energy igniter leads - dual circuits and off-engine mounted exciter unit

- On-engine mounted gas fuel injection manifolds.

- On-engine mounted water injection and liquid fuel manifold.

### AC Generator

- Two pole, Open Air Cooled (OAC) AC generator, 13.8kV, 3 phase, 60 Hz, 0.85 power factor in accordance with IEC 34-3 or ANSI C.50-14, fitted with class “F” insulation and designed for class “B” temperature rises with a brushless exciter.

- AC generator cooling system comprising air filter media, ducting and silencer and a generator shaft

### Gas Turbine Module

#### Enclosure and Base

- Fabricated weatherproof painted carbon steel baseplate mounted acoustic enclosure (85 dB(A) avg. @ 1m) and base for housing the gas turbine, inlet plenum, fuel and oil systems, exhaust volute and enclosure ventilation air systems.

- All internal lighting (main and emergency), maintenance power points, tubing, piping and cabling.

- Maintenance access and features, facilitating engine / module removal (sideways-removal from package) and in-situ maintenance.  Anchor points and any special tooling are provided.  Mechanical Handling Skid, standard walkways and ladders giving access to the inlet filter house are included.

- Fire protection and gas detection system, complete with thermal detectors and gas sensors for GT enclosure.

- Two-shot CO2 extinguishing system, including storage cylinders, manifold, fire dampers, pipe work to nozzles within the gas turbine compartment, warning lamps, lock-offs, interlocks and high temperature cabling.

- Dry diaphragm flexible coupling shaft including bolts.  A separate shaft guard is not required as the coupling shaft is protected by the cone arrangement in the exhaust diffuser.

#### Combustion Air System

- Self-cleaning (pulsed) combustion air intake filters with first stage coalesce.

- Pulsed cleaning control system fitted on the filter unit.  The air required for the pulse cleaning of the filter will be supplied by others.

- Combustion air inlet silencer and ducting, with flexible joints to accommodate thermal movement.

- Steel support structure mounted on the GT base, including access ladder up to the filter units.

- Maintenance features such as anchor points and permanent tooling (internal filter element hoist).

- Radial air intake scroll with compressor water wash supply rings.

#### Gas Turbine Exhaust System

- Gas turbine exhaust volute exhausting vertically.

#### Gas Turbine Enclosure Ventilation and Air Handling System

##### Enclosure Ventilation Intake System

- Air is drawn from the same filter house as the combustion air system.  A designated section of the filter house is used to supply air exclusively for ventilation.

- The system includes ducting, silencing and fire dampers.

##### Enclosure Ventilation Exhaust System

- Three 50% duty AC motor belt driven induced draft ventilation fans.

- Ventilation air exhaust fire dampers, silencer, ducting and weather hood.

##### Gas Turbine Bleed Air

- Bleed air exhaust ducting and silencer.

#### Gas Turbine Lube Oil System

- Gas turbine lube oil system including a stainless steel lube oil tank with thermostatically controlled electric heater (common with the hydraulic start system), mist eliminator, engine driven supply pumps, duplex oil filter, simplex water cooled plate oil cooler, stainless steel pipe work and fittings, associated valves and instrumentation.

#### Gas Turbine Hydraulic Control System

- Gas turbine hydraulic control oil system comprising of two 100% duty AC motor driven variable displacement pumps, stainless steel tank, oil mist separator, two 100% duty bladder type accumulators, duplex oil filter, simplex water cooled plate oil cooler, stainless steel pipe work and fittings, associated valves and instrumentation.

#### Gas Turbine Hydraulic Start System

- Gas turbine hydraulic start system comprising of one 100% duty AC motor driven variable displacement pump and fixed displacement charge pump in tandem, stainless steel pipe work and fittings, associated filters, valves and instrumentation.

#### Gas Turbine  Gas Fuel System.

- Gas fuel forwarding system, located to the side of the gas turbine, comprising of metering valves, high speed shutoff valves, last chance strainer, enclosure mounted fuel manifolds, stainless steel pipe work and fittings, associated valves and instrumentation.

### AC Generator Module

#### Enclosure and Base

- Fabricated carbon steel skid and acoustic enclosure housing the AC generator, cooling air system, exciter and line and neutral cubicles.  Access doors and hatches for maintenance.

- Two-shot CO2 extinguishing system, including storage cylinders, manifold, fire dampers, pipe work to nozzles within the gas turbine compartment, warning lamps, lock-offs, interlocks and high temperature cabling.

#### Generator Lube Oil System

- One lube oil system located adjacent/near to the AC Generator base comprising one shaft driven oil pump (mounted on the generator, one AC motor driven auxiliary oil pump, one AC motor driven jacking oil pump, one DC motor driven emergency lube oil pump for run down, duplex oil filter, carbon steel oil reservoir with mist eliminator, vent and thermostatically controlled electric heater, associated pipe work (stainless steel downstream of filters/carbon steel upstream), fittings, valves and instrumentation.

### Water Wash System

- One mobile gas turbine compressor cleaning system, suitable for unfired washing.  Attachment points for the water wash system are externally located on the outside of the Gas Turbine Base plate.

### Liquid Fuel System

- High pressure liquid fuel system comprising one main and one auxiliary AC electric motor driven fixed displacement, bent axis, axial piston pump, metering valves, high speed shutoff valves, stainless steel pipe work and fittings, associated valves and instrumentation.  The system is mounted on a freestanding skid to be located adjacent to the gas turbine module.

### Water Injection System (for Emissions Control)

- Water injection system comprising three (3) x 33% AC electric motor driven fixed displacement, bent axis, axial piston pumps, stainless steel pipework and fittings, associated simplex filters, valves and instrumentation.  The system is mounted on a freestanding skid to be located adjacent to the gas turbine module.

### Control System

- Human Machine Interface’s (HMI) – To be mounted in the remote control room, shipped loose for installation in the operator’s control room.  All control systems are accessible remotely via the HMI system.

- Gas turbine control system will be installed in the front of the package on the gas turbine base plate. The following is included in the on-skid Controls Scope of Supply:

- Package Control System (PCS)

- Engine Control System (ECS)

- Fire and Gas Protection System

- Vibration monitoring for all rotating equipment

- Temperature monitoring of all rotating equipment

- AC Generator Control/Protection Panel (GCP/GPP) comprising a two bay cubicle with automatic voltage regulator, generator metering and protective relay, automatic and manual synchronizing facility, with synchroscope and check synchronizer, free issued for installation by others.

### Special Tools

- Coupling alignment tool, gas turbine transportation stand, lifting beams and slings, packing case, protection cover, blanks and restraints will be supplied to protect the engine during transportation and installation at site.  These items remain the property of PDVSA and will be returned after installation is complete.

### Equipment Testing

- Gas turbine factory test.

- AC Generator factory test

- Sub-system factory flushing and pressure testing.

- Auxiliary motor testing.

- Instrument and power cable insulation and continuity tests.

### Training

- PDVSA Phase 1, 2 and 3 for PDVSA Scope of Supply, based at OEM Training Facility-(OPTIONAL)

### Installation & Commissioning

- Lump sum Technical Direction of Installation and Commissioning are offer as an Option.

- One set of special tooling required for the Gas Turbine Generating Package Operation and Maintenance

- ICS Manuals (paper format) in English.

### Documentation

- Three sets of O&M Manuals (CD format) in English.

- Project drawings and document list.

### Options (Budgetary)

- Availability guarantee - is offered as part of the Long Term Service Agreement

- Generator Rotor Withdrawal tool

- Freight FAS, Port of Export

- MCC / UPS

- Inlet Chiller Coil

Trent 60 Power Generation Package

Termination Points

| Interface Description | Terminal Points |
| --- | --- |
| Combustion Air | Inlet to intake filter house. |
| Compressed air | Compressed air connection at skid edge. |
| Exhaust Gas | Transition enclosure wall duct joint. Inlet and outlet flanges of silencer section |
| Ventilation | Enclosure vents outlets. |
| Mountings | Locations on skid base plates and all other structural members. |
| Fuel Gas | Inlet flange on side of base plate and vent flange on the roof of the enclosure. |
| Instrument Air | Inlet connection on engine base plate. |
| Lubricants | Filling points at lubricating oil tanks. Drains connections at oil tanks. |
| Drains | Drains system connections on all skids as necessary. |
| Grounding | Grounding terminals on skids. |
| Control and Instrumentation | Serial link connection between HMI and Package mounted control system. GCPP Terminal blocks in control panels and on-skid connections. |
| HV Electric Power | Line side terminals of AC generator. Neutral terminal of AC generator |
| Compressor Cleaning | Filling point of wash tanks. |
| Low Voltage Power | At terminals inside the MCC. |

Trent 60 Power Generation Package

Exclusions

MED does not accept responsibility for items or aspects of equipment which are outside the Scope of Supply defined above.  The following items are excluded from this proposal, unless offered as an option.

- Site grounding

- Lightning protection

- Compressed air supply

- All auxiliary power supplies

- All first fills

- All fuel supplies, fuel supply and treatment

- Water supply and treatment

- Installation & commissioning labor

- Demolition and/or removal of any existing equipment, structures and concrete.

- Installation tooling

- Instrumentation for site Performance Testing

- Site facilities

- Fire sprinklers or other fire protection devices which may be required by insurance regulations.

- Motor Control Center (Budgetary Option)

- Battery Back Up System (Budgetary Option)

- Switchgear

- Transformers (Auxiliary & Main)

- Control system housing, external to gas turbine package enclosure mounted equipment

- Control System integration with existing DCS

- Black Start Diesel GenSet

- AC Generator Rotor Withdrawal

- Fiscal metering

- Site facilities

- Operating and strategic spares

- Civil engineering design, embedment and works

- Grout

- Erection of equipment

- Civil engineering design of any kind

- All interconnecting pipe work and cabling, beyond termination points, including:

- All wiring and piping to and from skids

- Local Lighting

- Stack Lighting, Grounding Protection System

- Unloading at site

- Import Duties and Taxes

- Any and all permits or special clearances required by any government agency. This includes air pollution permits as well as Local building permits, construction permits, etc.

Attachment      Scheduled Date(s)

FCA MANUFACTURER’S SITE DELIVERY SCHEDULE

The following dates are for delivery dates as applicable to this contract. Under no circumstance shall any delivery date be prior to the receipt of a mutually agreed letter of credit, as defined in section 3.8 of the main contract. Delivery dates for the package requiring additional field modification for 50Hz to 60 Hz conversion of GenSet package:

| Item | Equipment Description | Delivery Lead Time |  |  |
| --- | --- | --- | --- | --- |
| 1 | Main Gas Turbine Skid, Generator without Line Side and Neutral Cubicle | April 30, 2010 |  |  |
| 2 | Gas Turbine | See Note 1 |  |  |
| 3 | Line Side and Neutral cubicle | June 30, 2010 |  |  |
| 4 | Equipment required to be installed for 50hz to 60 Hz Conversion | August 30, 2010 (See Note 2) |  |  |

Note 1 – The gas turbine will be delivered in accordance with the customer’s installation and commissioning schedule need date, not to exceed 60 days from Main Gas Turbine Skid Delivery.

Note 2 – Customer will be required to take into consideration appropriate field support labor and schedule to install equipment shipped to site directly for converting GenSet package from 50Hz to 60Hz application ready.

60 HERTZ CONVERSION OF PACKAGE (INSTALLATION AT FACORY OR POST FCA DELIVERY DEPENDING ON DELIVERY DATE OPTION SELECTED)

• 60 hertz compliant materials to be installed by Customer supplied. Scope of conversion to include, but not limited to,

- Exchange of Air Filter Vent Fans

- Exchange of Package Enclosure Lighting

- Exchange of UCP Lighting

- Exchange of Mineral Oil Heaters & Pump Motors

- Exchange of GT Lube Oil Heaters & Pump Motors

- Exchange of Liquid Fuel Forwarding Pump Motors

- Exchange of Package Heaters

- Exchange of F&G CO2 Skid Heaters

- Exchange of GT Hydraulic Start Motor

• Craft Labor for installation of conversion material to be provided by DERWICK

FUEL REQUIREMENTS

1    GENERAL

RR gas turbines have the ability to burn a wide range of gaseous fuels as shown in Table 1. These gases present a broad spectrum of properties due to both active and inert components. This specification is designed to define guidelines that must be followed in order to burn these fuels in an efficient, trouble-free manner, while protecting the gas turbine and supporting hardware.

Table 2 identifies the acceptable test methods to be used in determining gas fuel properties.

Notes:

- When considering the use of alternate fuels, provide details of the fuel constituents, fuel temperature, and expected engine usage conditions and operating characteristics to RR for evaluation and recommendations.

- Values and limits apply at the inlet of the gas fuel control module.

## Design Criteria

The following table outlines the criteria conditions at the proposed jobsite for the design of the equipment:

| Location | TBD |
| --- | --- |
| Elevation | TBD |
| Design Point Ambient Temperature / Relative Humidity | TBD |
| Primary Fuel Source | TBD |
| Secondary Fuel Source | TBD |
| Seismic Design Criteria (BOP Equipment) | TBD |
| Maximum Wind Speed (Wind Load), MPH | TBD |
| Near Field Noise at 3 ft horizontal and 5 ft vertical, dBA NOTE 1 | TBD |
| Far Field Noise, dBA NOTE 1 | TBD at 400 ft / TBD at 700 ft |

NOTE 1:  Far field noise is based on single-unit only operation.  Multiple units operating at the same time will have an impact on both near and far field noise levels.

# COMMERCIAL TERMS

## Basis of Pricing

### Validity

This proposal is valid until April 15, 2010.

### Taxes

No sales or use taxes have been included in this quotation.  These prices quoted exclude any federal, state or local taxes or fees which may be associated with the export, import or purchase of equipment and/or services.

## Price

One (1) RR Trent 60 Gas Turbine Generator Set including as described in the scope of supply.  All pricing is based on ex-works factory delivery unless otherwise stated.

All Equipment Subject to Previous Sale

GTG UNIT

Generators set price (Unit)……………………...US$ 32,500,000

## Wire Information

| BENEFICIARY: |  |
| --- | --- |
| BANK NAME: |  |
| BANK ADDRESS: |  |
| CITY, STATE, ZIP: |  |
| COUNTRY: |  |
| SWIFT CODE: |  |
| Routing Number / ABA Code: (For USA Vendors) |  |
| ACCOUNT NUMBER: (without IBAN details) |  |

## Payment Schedule

This proposal is based upon receipt of the following progress payments and a Contract Agreement by both Parties by the Validity date Seller may request at any time, Purchaser will demonstrate its financial capability to continue to carry out its obligations under this Contract.  This demonstration may require that Purchaser furnish adequate payment security.

| Mile-stone | Milestone Description | Evidence of Completion | Unit 1 | Terms of Payment |
| --- | --- | --- | --- | --- |
| 1 | Equipment Contract Signature | Receipt of signed Equipment Contract | 25% Contract Price | Payment 3 days from signature |
| 2 | Gas Turbine Package Skid available EXW | Notification of readiness to ship EXW Manufacturing Facility | 35% Contract Value | Draw on LOC |
| 3 | AC Generator Skid available EXW | Notification of readiness to ship EXW Manufacturing Facility | 35% Contract Value | Draw on LOC |
| 4 | Gas Turbine available EXW | Notification of readiness to ship EXW Manufacturing Facility | 5% Contract Value | Draw on LOC |

- Warranty

JTURBINES will provide a one (1) year warranty on the entire gas turbine generator package and any other balance of plant equipment provided.

- Terms & Conditions

This proposal shall be valid for fifteen (15) days; provided, however, the obligation to treat this proposal as confidential, and that it cannot be shared with any third party without the prior written consent of JTURBINES shall survive.

MDE and JTURBINES will negotiate in good faith to establish general terms and conditions that are usual and customary of the sale of these new equipments.

- Site Services

JTURBINES would be pleased to also provide a proposal for the installation, startup and commissioning of the facility.  This would include providing construction supervision as well as startup engineers for all equipment provided.

JTURBINES can also provide an experienced service representative to assist the operating personnel during the first two (2) months after the equipment goes online.

- Follow Up

Please contact the following person at JTURBINES for information regarding this proposal:

John A Johnson,

Director of International Sales

John@ J-Turbines.com

Office:  713.254.9299

- Attachment A