Subject:	Morichal Generation Scope of Work

Dear

Energy Parts Solutions is pleased to present this scope of work for the design, programming an installation of the 115kV and 13.8kVrelay protection for the two (2) new GE LM-6000 generators being installed at the Morichal Facility.

The scope of work will include new primary and backup protection and controls for the two generators G1 and G2, two Generator Step Up (GSU) transformers TX-3 and TX-4 and 115kv circuit breakers H1020 and H720.  The scope will include a new pre-engineered control house with lighting and power, free standing relay/control and metering panels, transformer on-line DGA monitors and interconnection control cabling between the 115kV yard, 13.8kV bus and the control house. All relays will be IEC 61850 compliant and manufactured by Schweitzer. The relay and metering panels will consist of free standing cabinets with swing out panels, prewired with test blocks and terminal blocks.  Shorting type blocks will be used for all CT leads.  All control wiring will be #12 awg with CT leads being #10 awg.  Each panel will have a separate fuse block for AC and DC power.

Interconnection cables will be installed between the existing control house and the new control house to have mimic operation of the H1020 and H720 circuit breakers.  The 50BF protection will be extended to the various bank circuit breakers for breaker failure protection. The metering and controls will be mapped to a new remote terminal unit utilizing DNP3.0 which can then be connected to the existing fiber ring.  Revenue metering will be on the 115kV side using ION 8800 meters; a meter will also be located on the station service transformer for net metering purposes.  All control switches will be Electroswitch, SCADA ready with lighted nameplate for indication and breaker coil monitoring.  Protective relays will be programmed, tested and functionally tested along with the control system following installation.

The enclosed One-Line diagram provides the proposed protection scheme for the two new generators interconnection to the existing 115kV yard.  The primary generator protection will be provided by a SEL-700G.  The 15kV generator breakers will be equipped with a SEL-351 for overcurrent protection and backup generator protection.  The station service feeder breakers will also be equipped with SEL-351 breakers for overcurrent protection.  Primary transformer protection will be provided by a SEL-487E Transformer Protection Relay.  The transformer backup protection will be provided by a SEL-787 Transformer Protection Relay.  The overcurrent and breaker failure protection for the 115kV breakers will be provided by SEL-351 relays.

PDVSA will be providing the new 115kV circuit breaker for the H1020 bay, the two 70/90MVA transformers, 13.8kV switchgear and LM6000 units.  All required yard excavation, foundations and installation of conduits or trench ways will be performed by PDVSA.  All existing 115kV equipment will be reused throughout the remainder of the yard.  BOP is by PDVSA.

Below is an outline of the scope of work required for the proposed 13.8kV and 115kV protection scheme for the two (2) new generators at the Morichal generating facility.

Electrical Design

- One Line diagram

- Three line diagram

- Schematic diagrams

- New panel layout/arrangement drawing

- New panel wiring diagrams and interconnect drawings

Transformer TX-3 Protection Cabinet

- SEL-487 Transformers Primary Protection

- SEL-787 Transformers Backup Protection

- ElectroSwitch LOR lockout relays

- FT-1 or FT-19R test switches for each relay and LOR

Transformer TX-4 Protection Cabinet

- SEL-487 Transformers Primary Protection

- SEL-787 Transformers Backup Protection

- ElectroSwitch LOR lockout relays

- FT-1 or FT-19R test switches for each relay and LOR

CB H720 Protection Cabinet

- SEL-351 115kV Overcurrent Protection

- ElectroSwitch 52CSR control relay

- ElectroSwitch LOR lockout relays

- FT-1 or FT-19R test switches for each relay and LOR

CB H1020 Protection Cabinet

- SEL-351 115kV Overcurrent Protection

- ElectroSwitch 52CSR control relay

- ElectroSwitch LOR lockout relays

- FT-1 or FT-19R test switches for each relay and LOR

Annunciator Cabinet

- Generator G1 Annunciator Panel

- Generator G2 Annunciator Panel

- Satellite clock

15kV Protection (located in 15kV Switchgear)

- SEL-700G Primary Generator Protection

- SEL-351 Generator Breaker Protection

- SEL-351 Feeder Breaker Protection

Metering Panel

- Generator G1 115kV Metering Ion 8800

- Generator G1 15kV (station service) Metering Ion 8800

- Generator G2 115kV Metering Ion 8800

- Generator G2 15kV (station service) Metering Ion 8800

Control House Enclosure – Pre-Engineered

- Battery Room

- 125VDC battery system

- Battery Charger

- Ventilation

- Convenience outlets and lighting

- Install  Transformer TX-3 Protection Cabinet

- Install Transformer TX-4 Protection Cabinet

- Install CB H720 Protection Cabinet

- Install CB H1020 Protection Cabinet

- Install Metering cabinet

- Install G1/G2 Annunciator Panel

Control Wiring

- Install of DC circuits in control house

- Install new control cabling from 15kV switchgear to Control House.

- Install new control cabling from switchyard current transformers Control House.

- Install new control cabling from circuit breakers H1020, H1120, H720 and H820 to Control House

- Install new control cabling from Transformers TX-3 and TX-4 to Control House.

- Terminate control wiring in new relay panels.

SCADA

- Provide and install RTU compatible with existing plant system and IEC 61850 compliant.

- Develop I/O points list.

TRANSFORMER ON-LINE DGA

- Provide and install Kelman TransFIX transformer monitor on each GSU.

- Develop program and I/O points list.

Relay Settings/Programs

- Develop Relay Protective Setting.

- Develop Programs for SEL relays.

- Develop testing and commissioning requirements for new relay protection schemes.

Testing/Commissioning

- Relay

  - Check tightness of connections

  - Functional test of each elements used in the protection scheme.

  - Verify operation of light-emitting diodes, display, and targets.

  - Check all internal logic functions used in the protection scheme.

  - Check all output contacts

  - Check operation of all active digital inputs

- Current Transformers

  - Check tightness of connections

  - Perform Insulation-resistance test of each current transformer and its secondary wiring with respect to ground at 1000 volts dc for one minute.

  - Perform a polarity test of each current transformer.

  - Perform a ratio-verification test

- Voltage Transfromers

  - Check tightness of connections

  - Perform insulation-resistance tests winding-to-winding and each winding-to-ground.

  - Perform a turns-ratio test on all tap positions

- Wire check of all protection and control circuits to ensure wiring is installed in accordance with design drawings

- Functional testing of all Protection and control circuits.

For your convenience we have attached the anticipated schedule for the activities that we have proposed in this document.  We are investigating how to decrease the schedule, and will continue to do so, once an official release is given.  We expect to be able to improve the schedule by 30 – 45 days, but every day is critical.

Pricing:

| Description | Cost (US$) |
| --- | --- |
| Engineering, Programming and expenses | $564,464.00 |
| Installation Labor | $303,360.00 |
| Testing/Commissioning | $210,000.00 |
| Material | $1,290,000.00 |
| Total Price | $2,367,824.00 |

The above referenced proposal represents our understanding of your requirements based on our engineering review conducted during the week of July 5th, 2010.  If for any reason you do not agree with the above proposed protection scheme please let us know immediately so that we can modify your proposal accordingly.  We look forward to assisting you with the proposed protection scheme.

Sincerely,