Subject:	Jusepin II Substation Scope of Work

Dear

Energy Parts Solutions (EPS) is pleased to present the following scope of work for the relay protection upgrades on the following Petróleos de Venezuela, S.A. (PDVSA) substations: Jusepin II and WILPRO AP/MP. The following proposal identifies the need to upgrade the existing 115kV line protection resulting from the upgrades at Furrial substation. The outdated Siemens, ABB REL316*4 and GE D60 line protection relays are no longer supported by the industry and with the additions to Furrial substation, the need to upgrade the existing 115kV line protection is imperative. The following proposal for engineering of the new 115kV line protection, and 13.8kV protection as requested, includes estimates for material, labor, testing, and commissioning as well.

The existing relay cabinets along with the wiring and terminal blocks are in good shape and are suitable for re-use. We propose to replace the swing doors of the cabinets with new custom doors housing the new protection systems. We have used this technique in the past for similar upgrades and its success has proven to be effective in keeping the cost low and achieving the necessary protection upgrades at the same time.  The scope of work will include new primary and backup protection and controls for 115kV lines at Jusepin II and WILPRO AP & MP. The scope will include new panel doors with SEL 421 & SEL 311L for distance, line differential, and directional over current protection for 115kV lines supplying Jusepin I, Furrial, GAS, and Amana, substation. The new SEL 421 will also be used for breaker failure protection. All 115kV metering will be replaced with ION 8800 meters with new test switches. WILPRO AP & MP will be protected by over current and under voltage using SEL 351S with the potential to be tied into a transfer trip scheme upon further evaluation. New Iniven digital multiplexers will replace the ABB Fox 6Plus and GE FSC fiber multiplexers.

The scope of work also includes the 13.8kV protection upgrades at Jusepin II replacing transformer protection with a primary and backup SEL 787 and SEL 581 differential and over current relays; new Kelman on-line DGA monitors for each transformer; and new LTC voltage controllers and positioning indicators. The 13.8kV switchgear protection will also be upgraded by installing new swing panel doors equipped with SEL 351S and Electro Industry metering.  All relays will be IEC 61850 compliant and manufactured by Schweitzer. A new substation control centered on the SEL 3354 with HMI will be installed at Jusepin II. The new substation control will have the ability to be integrated into an existing SCADA system. All required yard excavation, foundations and installation of conduits or trench ways will be performed by PDVSA.

Jusepin II Substation:

Electrical Design

- Revisions to One Line diagram

- Revisions to Three line diagram

- Schematic diagrams

- New panel layout/arrangement drawing

- Revisions to panel wiring diagrams and interconnect drawings

115kV Line Protection Relay Panels (R2, R4, R5, R6, R7) for GAS, Furrial, Amana, & Juespin I lines. (115kV Panel R3 to remain)

- Remove swing panel door including relays.

- New custom swing panel door.

- SEL 421 distance, over current, directional over current relays.

- SEL 311L line differential relays.

- ElectroSwitch LOR lockout relays.

- FT-1 or FT-19R test switches for each relay.

115kV Bus Protection Panel (RB)

- Remove swing panel door including relays.

- New custom swing panel doors.

- SEL-487B 115kV Bus Different relay

- SEL 581 Differential (Backup)

- ElectroSwitch LOR lockout relays

- FT-1 or FT-19R test switches for each relay and LOR

115kV Breaker Protection Panels (R13)

- Remove swing panel door including relays.

- New custom swing panel door.

- SEL-351S 115kV over current and control relay.

- ElectroSwitch LOR lockout relays

- FT-1 or FT-19R test switches for each relay and LOR

115kV Line Protection Communication

- Remove ABB Fox 6PLUS and GE FSC multiplexers.

- New Iniven digital multiplexer.

115kV Metering for GAS, Amana, Furrial, and Spare

- Remove swing panel door including relays.

- New custom swing panel door.

- ION 8800 meters.

- FT-1 or FT-19R test switches for each meter.

Transformer Protection Panels (T3 & T4)

- Remove swing panel door including relays.

- New custom swing panel doors.

- SEL 787 transformer protection relay with over current and differential.

- SEL 587 differential with over current as backup relay.

- Beckwith M2270 and M2001 LTC voltage controllers.

- LTC indication positioning.

- FT-1 or FT-19R test switches for each relay.

Transformer On-Line DGA (2 Units Tx3 & Tx4)

- Kelman TapTrans transformer monitors.

- Develop program and I/O points list.

13.8kV Switchgear Protection and Control

- Remove swing panel door including relays.

- SEL 351S over current, synchronism check, and breaker control relays.

- Electro Industry Meters.

- FT-1 or FT-19R test switches for each relay.

- ElectroSwitch LOR lockout relays

- ElectroSwitch 52CRS control switch

Substation Control Unit and SCADA integration

- Develop I/O points list.

- SEL 3354 Automated Computing Platform with Human Machine Interface.

- Interface to upgraded 115kV and 13.8kV relays and meters.

Relay Settings/Programs

- Develop Relay Protective Setting.

- Develop Programs for SEL relays.

- Develop Programs for Kelman units.

- Develop testing and commissioning requirements for new relay protection schemes.

Testing/Commissioning

- Relay

  - Check tightness of connections

  - Functional test of each elements used in the protection scheme.

  - Verify operation of light-emitting diodes, display, and targets.

  - Check all internal logic functions used in the protection scheme.

  - Check all output contacts

  - Check operation of all active digital inputs

- Current Transformers

  - Check tightness of connections

  - Perform Insulation-resistance test of each current transformer and its secondary wiring with respect to ground at 1000 volts dc for one minute.

  - Perform a polarity test of each current transformer.

  - Perform a ratio-verification test

- Voltage Transfromers

  - Check tightness of connections

  - Perform insulation-resistance tests winding-to-winding and each winding-to-ground.

  - Perform a turns-ratio test on all tap positions

- Wire check of all protection and control circuits to ensure wiring is installed in accordance with design drawings

- Functional testing of all Protection and control circuits.

GAS (WILPRO AP and WILPRO MP) Substations:

Electrical Design

- Revisions to One Line diagram

- Revisions to Three line diagram

- Schematic diagrams

- New panel layout/arrangement drawing

- Revisions to panel wiring diagrams and interconnect drawings

115kV Line Protection Relay Panels

- Remove entire swing panel door with relays, test switches, and annunciators attached.

- New custom swing panel doors.

- SEL 351S overcurrent and control relays.

- ElectroSwitch LOR lockout relays.

- FT-1 or FT-19R test switches for each relay.

Relay Settings/Programs

- Develop Relay Protective Setting.

- Develop Programs for SEL relays.

- Develop testing and commissioning requirements for new relay protection schemes.

Testing/Commissioning

- Relay

  - Check tightness of connections

  - Functional test of each elements used in the protection scheme.

  - Verify operation of light-emitting diodes, display, and targets.

  - Check all internal logic functions used in the protection scheme.

  - Check all output contacts

  - Check operation of all active digital inputs

- Current Transformers

  - Check tightness of connections

  - Perform Insulation-resistance test of each current transformer and its secondary wiring with respect to ground at 1000 volts dc for one minute.

  - Perform a polarity test of each current transformer.

  - Perform a ratio-verification test

- Voltage Transfromers

  - Check tightness of connections

  - Perform insulation-resistance tests winding-to-winding and each winding-to-ground.

  - Perform a turns-ratio test on all tap positions

- Wire check of all protection and control circuits to ensure wiring is installed in accordance with design drawings

- Functional testing of all Protection and control circuits.

We are working on producing a schedule for this project.  Currently we are waiting on equipment delivery confirmation from two vendors.  Once we have this information we will send it immediately over to you.  However, as you can see from the proposal there is a large amount of engineering that needs to be completed prior to ordering the materials.  In order to minimize the schedule impact we ask that you evaluate our proposal as soon as possible and give us the proper instruction on whether or not to start engineering.

Pricing:

| Description | Cost (US$) |
| --- | --- |
| Engineering | $1,385,900 |
| Installation Labor | $289,000 |
| Testing/Commissioning | $529,000 |
| Material | $1,899,000 |
|  | $4,102,900 |

The above referenced proposal represents our understanding of your requirements based on our engineering review conducted during the week of July 5th, 2010.  If for any reason you do not agree with the above proposed protection scheme please let us know immediately so that we can modify your proposal accordingly.  We look forward to assisting you with the proposed protection scheme.