INSPECTION REPORT

2003/ Reg. No. 2003/003620/07

# B.I.E. International Engineers (Pty) Ltd

P O Box 603, Florida Hills, 1716

2 Bergbron, Northcliff

Tel:  (011) 477 2212 Fax:  (011) 477-5523  Email: mikes@bie.co.za

Job No: M1120

Date: 22 February 2010

| SURVEILLANCE | #### X |  | REJECTION |  | RELEASE |  |
| --- | --- | --- | --- | --- | --- | --- |

| Customer: | PDVSA Services | Supplier: | Derwick Associates |
| --- | --- | --- | --- |
| Contract Site: | Ubungo Maziwa Road Tanzania | Assignment Number: | 2232 |
| Order No: | 510 007 7213 | Assignment Date: | 04 Dec 2009 |
| Work / Req No. | UD 640 05412 | Co ordinator: | Leiro Medina |

| ##### Activities |  |  |  |
| --- | --- | --- | --- |
| Date Order Placed: | 04 Dec 2009 | # Forecast Delivery Date: | # TBA |
| Contractual/Delivery Date: | 31 March 2010 | # Actual Delivery Date: | # TBA |

| QCP No | Ref No | Drawing No | Rev | Description | Qty | Activity | Acc/Rej | Report/ Certificate No | Accept Criteria |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| N/A | 0 | N/A |  | 4X TM 2 500 | 4 | Surveillance | N/A | 1 | Inspection request |

Remarks/Comments:

Summary: A visit to inspect 4 x TM 2 500 at Dowans Ubungo Maziwa Road, Tanzania

Purpose of visit: To evaluate the operational condition of the 4 x TM 2 500 gas turbines

lnspection Conducted: Visual inspection of all equipment with photographs was done, make reference to the continuation report

Results of lnspection: All 4 TM 2 500 were as follows: TM 41, TM 42, TM 43 seemed to be in good operational order but TM 40 turbine needs refurbishing as noted in the borescope done by Pro energy on the 9th of August 2009

Specifications/ : Maintenance manuals numbers 1 – 18 were available{2 copies} Maintenance

Electrical Drawings: A complete set was available for each of the TM 2 500

TM 2 500 Performance : A report was drawn off from each of the 4 TM 2 500 when they Report were in operation. Refer to Appendix 1.

High Crank: A high crank was done on all 4 TM 2 500 and a report was drawn for Each one. Refer to Appendix 2.

### CONTINUATION REPORT

Remarks/Comments:

The overall view of the above equipment was found to be very satisfactory and appeared to be in operational conditional. The TM – 40 at site B needs some refurbishing on the gas turbine side {refer to borescope inspection dated August 2009.}

Control Room : The control rooms in all 4 TM 2 500 were found to be in excellent condition, the control cubicals were complete with all the necessary equipment i. e - Digital Synchronisation – the power analyser is in good working order and able to read the values of voltage current power and power factor on each of the phases. Refer to reports. - Excitation controller seems to be in good condition. Brush Prismic A30 - Generator Protection System or Integrated Protection System is in good working condition. - Micronet digital control system is functioning as it should be { this is the main frame computer}. - Rotor earth fault monitor is in circuit with the relevant equipment. - Vibration monitor unit Bently Navada 3500 was found in TM 41, 42, 43. TM 40 had a Bently Navada 3300. - The fire and gas protection unit in good monitoring order. - 24 volt / 25 amps bank of batteries with charger for the fire and gas control systems permanently energized. This system has a disconnect switch. - 24 volts/ 150 amp bank of batteries with a charger. This is used in all the control circuit for the turbine and a generator. This two has a disconnect switch, the control circuit are presently energized and the safety equipment is operational. - 125 volts DC / 25 amps bank of batteries with a charger, this voltage is used to start a 125 VDC motor for the purpose of lubricating the generator bearings. - A step down transformer is used for lighting purposes - A termination cubical is neatly and clearly marked - All senses for the protection of the generator and the turbine are in place and wired back to the control room for monitoring.

It was requested that a high crank procedure be initiated on all 4 TM 2500.This was done via the HMI {PC interface} The sequence for starting the turbine was witnessed and found to be in order. With no gas or fuel available to start, the hydraulic lube oil motor for starting the turbine was used. All 4 units where run for 5 minutes each at plus minus 2400 rpm. After 5mins the hydraulic oil cooler fans started in sequence, the purpose was to cool both the turbine and the generator this continued for 15minutes. The 3 turbine cooling fans started sequentially and ran for the full duration. The overall view of the TM 40, TM41, 42, 43 gas turbines indicate that they are in a good operational condition.

Please note:

No certificates of manufacture were available

No commissioning certificates were available at manufacture level No calibration certificates were available No polarisation index {PI} was available at manufacture level or subsequent to manufacture

Operation reports are available dating back to July 2008 for the TM 40, 41, 42, 43. This was supplied by plant operator. These will be sent via courier. Plant performance test were provided. This will be sent via courier. The high crank report for TM 40, 41, 42, 43 and this will be sent courier.

Photographs attached

1 – Complete unit showing chillers, turbine and generator

2- Control room exterior

3 - Generator

4 – Siemens breaker and generator

| STATUS DOCUMENTS |  |
| --- | --- |
| Drawings: 4 x Complete set available | Design Review:N/A |
| QCP’s:N/A | Spares/Operating Manuals: Manuals 1-18 available. |
| Calculations:N/A | Data Book: not available |
| Bar Chart:N/A | Other: |

| SUPPLIER REPRESENTATIVE: | PRINT NAME: ## Not Present | SIGN: |
| --- | --- | --- |
| B.I.E. SURVEYOR: | PRINT NAME: M.B. Megaw | SIGN: |